## parameters
| version | converged | name | f_hz | sn_mva | pf_converged
0 | 2.9.0 | FALSE | Dorf | 50 | 100 | FALSE

## bus
| name | vn_kv | type | zone | in_service | description | substat | folder_id | sernum | for_name | chr_name
14854 | 7091091_001001_001001_00550055_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | D7F954013E6F4D0DA6F141126D2B5678
13846 | 7091091_001001_001001_00500050_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 4C90447FCDE84E1E9BA89D818E1A003C
23081 | 7091091_001001_001001_00670067_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
29243 | 7091091_001001_001001_00260026_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
13888 | 7091091_001001_001001_00680068_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 3F22D947513B4292983EEC7A179B9A8F
23128 | 7091091_001001_001001_00220022_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
23129 | 7091091_001001_001001_00230023_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
25191 | 7091091_001001_001001_00370038_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
21610 | 7091091_001001_001001_00530053_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
20588 | 7091091_001001_001001_00160016_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 0159890C1AAC48459E1F26EF2F7A15DF
21623 | 7091091_001001_001001_00080008_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
16503 | 7091091_001001_001001_00190019_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | FA2D966972F94931A6EB55F8EB518BFC
24189 | 7091091_001001_001001_00300030_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
24190 | 7091091_001001_001001_00290029_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
16517 | 7091091_001001_001001_00020004_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 3F482191034B406A8B88B10F18572CD5
24723 | 7091091_001001_001001_00100010_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
26773 | 7091091_001001_001001_00570057_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
22166 | 7091091_001001_000000_00010001_02001 | 0.4 | b | SWF | TRUE | #REF! |  | SWF
26774 | 7091091_001001_001001_00570058_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
22165 | 7024024_001001_005005_02120212_01127 | 21 | b | SWF | TRUE | #REF! |  | SWF
20128 | 7091091_001001_001001_00360036_01002 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | B8A6B8034CC946A8A42DF56445E253CC
33442 | 7091091_001001_001001_00610061_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
14505 | 7091091_001001_001001_00660066_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 5B050C0F95C84233BCA9E81506F7AD51
20652 | 7091091_001001_001001_00540054_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | E40A71EE8E5E47838DA77CE02AF35955
28854 | 7091091_001001_001001_00390039_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
30390 | 7091091_001001_001001_00450045_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
17087 | 7091091_001001_001001_00380038_01002 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 0500561E945B4175B5CCAF16DC47C318
25791 | 7091091_001001_001001_00510051_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
16582 | 7091091_001001_001001_00620062_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | BD86A46F9F8D495E9080EE159BDA6F13
20680 | 7091091_001001_001001_00520052_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 904FFBFFE73B4603BED6FB2281DE1CE4
27337 | 7091091_001001_001001_00310031_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
27338 | 7091091_001001_001001_00320032_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
23763 | 7091091_001001_001001_00350035_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
23764 | 7091091_001001_001001_00350036_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
13014 | 7091091_001001_001001_00110011_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 1B4DA75F1D5B4B3C93D699185615DD6E
23256 | 7091091_001001_001001_00060006_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
19705 | 7091091_001001_001001_00070007_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | A1DC4B40F8B3446E971DD4F125C30933
17155 | 7091091_001001_001001_00640064_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 9E36004BD0EA42D59F6C0F1FF32BAA63
21767 | 7091091_001001_001001_00410041_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
13076 | 7091091_001001_001001_00600060_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 2626FC43A4934DC79CDF1325A60B9F99
30999 | 7091091_001001_001001_00690069_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
26400 | 7091091_001001_001001_00330033_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
26401 | 7091091_001001_001001_00340034_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
20267 | 7091091_001001_001001_00710071_01002 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 2EE05127BC1F4068BA2C37EE07D19501
22836 | 7091091_001001_001001_00240024_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
18229 | 7091091_001001_001001_00030003_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 1C2B1038D5EF4D519106D3D41599A6DF
22837 | 7091091_001001_001001_00250025_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
23873 | 7091091_001001_001001_00080018_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
17221 | 7091091_001001_001001_00180018_01002 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 59B142ACF09949FB95AB8F05B3F2CFD9
25929 | 7091091_001001_001001_00370037_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
25422 | 7091091_001001_001001_00440044_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
27474 | 7091091_001001_001001_00690071_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
30059 | 7091091_001001_001001_00040004_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
17261 | 7091091_001001_001001_00560056_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | F8F04373BB5F4B36B82206C0638308B1
29550 | 7091091_001001_001001_00490049_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
13174 | 7091091_001001_001001_00400040_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | B632A01E1D5D41F29988DC3D852D40D1
33146 | 7091091_001001_001001_00020008_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
24978 | 7091091_001001_001001_00470047_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
14739 | 7091091_001001_001001_00270027_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 208A8B1B7E0941DDA96D1CD436CBCE5E
24979 | 7091091_001001_001001_00480048_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
26522 | 7091091_001001_001001_00420042_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
24987 | 7091091_001001_001001_00050005_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
24988 | 7091091_001001_001001_00050014_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
28578 | 7091091_001001_001001_00120012_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
23463 | 7091091_001001_001001_00170017_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
25512 | 7091091_001001_001001_00590059_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
24489 | 7091091_001001_001001_00430043_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
19889 | 7091091_001001_001001_00140014_01002 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 1120AC86372248A8ADA9CE3DCA1613CF
21943 | 7091091_001001_001001_00020002_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  |  | 63
30136 | 7091091_001001_001001_00630063_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
14786 | 7091091_001001_001001_00700070_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | F1AB5C76A10D455FAAA5CD3BAE2056EF
14787 | 7091091_001001_001001_00460046_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | C09B7CEEBA6D4FBE9F3EAFDEC87E3B67
20423 | 7091091_001001_001001_00580058_01002 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | DA1C2CE153E54853A2CC73E8FB89E908
17868 | 7091091_001001_001001_00150015_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | 6B5F20F8B1504814B7F39DDDEB923A0C
18894 | 7091091_001001_001001_00130013_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF |  | A7F3EA6F44664381BBD82C495CBD0CF0
32722 | 7091091_001001_001001_00010002_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
24051 | 7091091_001001_001001_00280028_01001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
24052 | 7091091_001001_001001_00210021_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF
28155 | 7091091_001001_001001_00650065_03001 | 0.4 | m | SWF | TRUE | #REF! |  | SWF

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | description | sernum | for_name | chr_name | 2021
20640 | 7091091_001001_001001_00180018_08001 | 17221 | 1.7455e-05 | 3.5444e-06 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:ctsp,sub_type:office,dummy:False,demand:19.523,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 17455.0 kWh 2020: 17560.0 kWh 2021: 19523 kWh
20642 | 7091091_001001_001001_00110011_08001 | 13014 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:14.496,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 7961.0 kWh 2020: 18313.0 kWh 2021: 14496 kWh
20643 | 7091091_001001_001001_00110011_08002 | 13014 | 0.000505 | 7.1959e-05 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.007,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2.0 kWh 2020: 4.0 kWh 2021: 7 kWh
20644 | 7091091_001001_001001_00110011_08003 | 13014 | 0.00014308 | 2.9054e-05 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:industry,sub_type:storage,dummy:False,demand:133.764,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 143081.0 kWh 2020: 137614.0 kWh 2021: 133764 kWh
20646 | 7091091_001001_001001_00550055_08001 | 14854 | 0.002055 | 0.00029282 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.048,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2519.0 kWh 2020: 2152.0 kWh 2021: 2048 kWh
20647 | 7091091_001001_001001_00550055_08002 | 14854 | 0.00228 | 0.00032488 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.13,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1882.0 kWh 2020: 2062.0 kWh 2021: 2130 kWh
20648 | 7091091_001001_001001_00550055_08003 | 14854 | 0.002055 | 0.00029282 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.048,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2519.0 kWh 2020: 2152.0 kWh 2021: 2048 kWh
20649 | 7091091_001001_001001_00680068_08001 | 13888 | 0.006982 | 0.00099488 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:7.476,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 6206.0 kWh 2020: 7270.0 kWh 2021: 7476 kWh
20650 | 7091091_001001_001001_00680068_08002 | 13888 | 0.006982 | 0.00099488 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:7.476,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 6206.0 kWh 2020: 7270.0 kWh 2021: 7476 kWh
20651 | 7091091_001001_001001_00460046_08001 | 14787 | 0.002598 | 0.00037019 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:5.599,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 5059.0 kWh 2020: 5220.0 kWh 2021: 5599 kWh
20652 | 7091091_001001_001001_00640064_08001 | 17155 | 0.002687 | 0.00038288 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:4.403,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3728.0 kWh 2020: 4508.0 kWh 2021: 4403 kWh
20653 | 7091091_001001_001001_00640064_08002 | 17155 | 5.4e-05 | 7.6946e-06 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.011,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 21.0 kWh 2020: 21.0 kWh 2021: 11 kWh
20654 | 7091091_001001_001001_00640064_08003 | 17155 | 0.002687 | 0.00038288 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:4.403,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3728.0 kWh 2020: 4508.0 kWh 2021: 4403 kWh
20655 | 7091091_001001_001001_00620062_08001 | 16582 | 0.002042 | 0.00029097 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:2.498,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1948.0 kWh 2020: 2412.0 kWh 2021: 2498 kWh
20656 | 7091091_001001_001001_00150015_08001 | 17868 | 0.001397 | 0.00019906 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.661,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 572.0 kWh 2020: 658.0 kWh 2021: 661 kWh
20657 | 7091091_001001_001001_00150015_08002 | 17868 | 0.003102 | 0.00044201 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.143,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2995.0 kWh 2020: 3421.0 kWh 2021: 3143 kWh
20658 | 7091091_001001_001001_00150015_08003 | 17868 | 0.001337 | 0.00019051 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:1.047,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1004.0 kWh 2020: 1040.0 kWh 2021: 1047 kWh
20659 | 7091091_001001_001001_00520052_08001 | 20680 | 0.00257 | 0.00036621 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:1.799,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1653.0 kWh 2020: 1679.0 kWh 2021: 1799 kWh
20660 | 7091091_001001_001001_00520052_08002 | 20680 | 0.00257 | 0.00036621 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:1.799,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1653.0 kWh 2020: 1679.0 kWh 2021: 1799 kWh
20661 | 7091091_001001_001001_00700070_08001 | 14786 | 0.000505 | 7.1959e-05 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.817,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 0.0 kWh 2020: 322.0 kWh 2021: 817 kWh
20662 | 7091091_001001_001001_00700070_08002 | 14786 | 0.002268 | 0.00032317 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.253,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3088.0 kWh 2020: 3199.0 kWh 2021: 3253 kWh
20663 | 7091091_001001_001001_00700070_08003 | 14786 | 0.002268 | 0.00032317 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.253,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3088.0 kWh 2020: 3199.0 kWh 2021: 3253 kWh
20664 | 7091091_001001_001001_00710071_08001 | 20267 | 0.002776 | 0.00039556 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.127,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2470.0 kWh 2020: 1994.0 kWh 2021: 2127 kWh
20665 | 7091091_001001_001001_00710071_08002 | 20267 | 0.002776 | 0.00039556 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.127,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2470.0 kWh 2020: 1994.0 kWh 2021: 2127 kWh
20666 | 7091091_001001_001001_00660066_08001 | 14505 | 0.000257 | 3.662e-05 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.404,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 243.0 kWh 2020: 2346.0 kWh 2021: 2404 kWh
20667 | 7091091_001001_001001_00660066_08002 | 14505 | 0.001271 | 0.00018111 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.594,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2343.0 kWh 2020: 2488.0 kWh 2021: 2594 kWh
20668 | 7091091_001001_001001_00580058_08001 | 20423 | 0.001773 | 0.00025264 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.1,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1768.0 kWh 2020: 2017.0 kWh 2021: 2100 kWh
20669 | 7091091_001001_001001_00580058_08002 | 20423 | 0.001799 | 0.00025634 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.67,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1479.0 kWh 2020: 1080.0 kWh 2021: 670 kWh
20670 | 7091091_001001_001001_00580058_08003 | 20423 | 0.001773 | 0.00025264 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.1,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1768.0 kWh 2020: 2017.0 kWh 2021: 2100 kWh
20671 | 7091091_001001_001001_00560056_08001 | 17261 | 0.002384 | 0.0003397 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.863,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2779.0 kWh 2020: 2779.0 kWh 2021: 2863 kWh
20672 | 7091091_001001_001001_00560056_08002 | 17261 | 0.000947 | 0.00013494 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:9.362,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3471.0 kWh 2020: 3471.0 kWh 2021: 9362 kWh
20673 | 7091091_001001_001001_00540054_08001 | 20652 | 0.002456 | 0.00034996 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.689,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3071.0 kWh 2020: 3031.0 kWh 2021: 3689 kWh
20674 | 7091091_001001_001001_00540054_08002 | 20652 | 0.002507 | 0.00035723 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.373,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3137.0 kWh 2020: 3356.0 kWh 2021: 3373 kWh
20675 | 7091091_001001_001001_00540054_08003 | 20652 | 0.002456 | 0.00034996 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.689,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3071.0 kWh 2020: 3031.0 kWh 2021: 3689 kWh
20676 | 7091091_001001_001001_00540054_08004 | 20652 | 0 | 0 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.049,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: nan kWh 2020: nan kWh 2021: 49 kWh
20677 | 7091091_001001_001001_00380038_08001 | 17087 | 0.002731 | 0.00038915 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.235,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3431.0 kWh 2020: 3069.0 kWh 2021: 2235 kWh
20678 | 7091091_001001_001001_00380038_08002 | 17087 | 0.001717 | 0.00024466 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:1.127,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1177.0 kWh 2020: 1186.0 kWh 2021: 1127 kWh
20679 | 7091091_001001_001001_00380038_08003 | 17087 | 0.00141 | 0.00020091 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.884,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 505.0 kWh 2020: 2230.0 kWh 2021: 884 kWh
20680 | 7091091_001001_001001_00380038_08004 | 17087 | 0 | 0 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.007,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: nan kWh 2020: 12.0 kWh 2021: 7 kWh
20681 | 7091091_001001_001001_00380038_08005 | 17087 | 0.001717 | 0.00024466 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:1.127,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1177.0 kWh 2020: 1186.0 kWh 2021: 1127 kWh
20682 | 7091091_001001_001001_00140014_08001 | 19889 | 0.000246 | 3.5053e-05 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.295,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 341.0 kWh 2020: 299.0 kWh 2021: 295 kWh
20683 | 7091091_001001_001001_00140014_08002 | 19889 | 0.001981 | 0.00028228 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.46,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2244.0 kWh 2020: 2240.0 kWh 2021: 2460 kWh
20684 | 7091091_001001_001001_00140014_08003 | 19889 | 0.001455 | 0.00020733 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:1.538,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1510.0 kWh 2020: 1565.0 kWh 2021: 1538 kWh
20685 | 7091091_001001_001001_00140014_08004 | 19889 | 0.001271 | 0.00018111 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.529,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2336.0 kWh 2020: 2537.0 kWh 2021: 2529 kWh
20686 | 7091091_001001_001001_00140014_08005 | 19889 | 0.001271 | 0.00018111 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:2.529,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 2336.0 kWh 2020: 2537.0 kWh 2021: 2529 kWh
20687 | 7091091_001001_001001_00600060_08001 | 13076 | 0.003156 | 0.0004497 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:5.237,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 4600.0 kWh 2020: 3964.0 kWh 2021: 5237 kWh
20688 | 7091091_001001_001001_00500050_08001 | 13846 | 0.001512 | 0.00021545 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:3.418,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1909.0 kWh 2020: 2132.0 kWh 2021: 3418 kWh
20689 | 7091091_001001_001001_00190019_08001 | 16503 | 6.1548e-05 | 1.2498e-05 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:ctsp,sub_type:retail,dummy:False,demand:52.002,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 61548.0 kWh 2020: 58288.0 kWh 2021: 52002 kWh
20691 | 7091091_001001_001001_00360036_08001 | 20128 | 0.003295 | 0.00046951 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.258,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3361.0 kWh 2020: 2534.0 kWh 2021: 3258 kWh
20692 | 7091091_001001_001001_00360036_08002 | 20128 | 0.003295 | 0.00046951 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:3.258,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 3361.0 kWh 2020: 2534.0 kWh 2021: 3258 kWh
20693 | 7091091_001001_001001_00160016_08001 | 20588 | 0.001924 | 0.00027416 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.54,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1631.0 kWh 2020: 382.0 kWh 2021: 540 kWh
20694 | 7091091_001001_001001_00160016_08002 | 20588 | 0.001924 | 0.00027416 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,dummy:False,demand:0.54,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 1631.0 kWh 2020: 382.0 kWh 2021: 540 kWh
24398 | 7091091_001001_001001_00400040_08001 | 13174 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:8.398,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
24678 | 7091091_001001_001001_00270027_08001 | 14739 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:8.398,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25007 | 7091091_001001_001001_00020004_08001 | 16517 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:8.398,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25329 | 7091091_001001_001001_00030003_08001 | 18229 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:8.398,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25452 | 7091091_001001_001001_00130013_08001 | 18894 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:8.398,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25617 | 7091091_001001_001001_00070007_08001 | 19705 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,dummy:False,demand:8.398,file:NaN,file_add:NaN,cos_phi:0.98,load_type:inflexible_load |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25618 | 7091091_001001_001001_00070007_08001 | 19705 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,owner:25617,demand:8.398,file:NaN,cop_file:cop.csv,cos_phi:0.98,load_type:hp,power:0.087 |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25619 | 7091091_001001_001001_00070007_08001 | 19705 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,owner:25617,demand:8.398,file:NaN,file_add:driving.csv,cos_phi:0.98,load_type:ev,capacity:0.085,consumption:0.018,charging_home:0.0072,charging_ac:0.011,charging_dc:0.150,efficiency:0.9,soc:0.8,v2g:False,v2h:False |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25620 | 7091091_001001_001001_00070007_08001 | 20128 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,owner:20691,demand:8.398,file:NaN,cop_file:cop.csv,cos_phi:0.98,load_type:hp,power:0.0150 |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25621 | 7091091_001001_001001_00070007_08001 | 17261 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,owner:20672,demand:8.398,file:NaN,file_add:driving.csv,cos_phi:0.98,load_type:ev,capacity:0.085,consumption:0.018,charging_home:0.0072,charging_ac:0.011,charging_dc:0.150,efficiency:0.9,soc:0.8,v2g:False,v2h:False |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25622 | 7091091_001001_001001_00070007_08001 | 19705 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,owner:25617,demand:8.398,file:NaN,heat_file:heat.csv,load_type:heat,temperature:55 |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25623 | 7091091_001001_001001_00070007_08001 | 19705 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:sfh,owner:25617,demand:8.398,file:NaN,heat_file:dhw.csv,load_type:dhw,temperature:55 |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25624 | 7091091_001001_001001_00070007_08001 | 17261 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,owner:20672,demand:8.398,file:NaN,heat_file:heat.csv,load_type:heat,temperature:55 |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast
25625 | 7091091_001001_001001_00070007_08001 | 17261 | 0.006444 | 0.00091822 | 0 | 0 |  | 0.001 | TRUE | wye | agent_type:mfh,owner:20672,demand:8.398,file:NaN,heat_file:dhw.csv,load_type:dhw,temperature:55 |  |  |  | 2019: 7904.331929613476 kWh 2020: 8216.51088218224 kWh 2021: 8397.502809778027 kWh Ersatzlast

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source | description | sernum | for_name | chr_name
86 | 7091091_001001_001001_00190019_09001 | 16503 | 0.0102 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:20689,power:0.0102,file:NaN,cos_phi:0.99,orientation:1,angle:35
130 | 7091091_001001_001001_00500050_09001 | 13846 | 0.0055 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:20688,power:0.0055,file:NaN,cos_phi:0.99,orientation:10,angle:75
232 | 7091091_001001_001001_00180018_09001 | 17221 | 0.01216 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:20640,power:0.0122,file:NaN,cos_phi:0.99,orientation:15,angle:40
281 | 7091091_001001_001001_00190019_09002 | 16503 | 0.025 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:20690,power:0.025,file:NaN,cos_phi:0.99,orientation:-1,angle:5
484 | 7091091_001001_001001_00020004_09001 | 16517 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:25007,power:0.16,file:NaN,cos_phi:0.99,orientation:-30,angle:25
494 | 7091091_001001_001001_00140014_09001 | 19889 | 0.0298 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:20683,power:0.0298,file:NaN,cos_phi:0.99,orientation:-5,angle:32
568 | 7091091_001001_001001_00710071_09001 | 20267 | 0.009 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:20664,power:0.009,file:NaN,cos_phi:0.99,orientation:11,angle:33
485 | 7091091_001001_001001_00020004_09001 | 16517 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:battery,owner:25007,power:0.16,file:NaN,cos_phi:0.99,capacity:0.192,efficiency:0.95,soc:0.5,g2b:False,b2g:False
495 | 7091091_001001_001001_00140014_09001 | 19889 | 0.0298 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:wind,owner:20683,power:0.0298,file:NaN,cos_phi:0.99,height:30
496 | 7091091_001001_001001_00140014_09001 | 19889 | 0.0298 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:fixed_gen,owner:20683,power:0.0298,file:NaN,file_add:NaN
497 | 7091091_001001_001001_00140014_09001 | 19889 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:battery,owner:20683,power:0.16,file:NaN,cos_phi:0.99,capacity:0.192,efficiency:0.95,soc:0.5,g2b:False,b2g:False
233 | 7091091_001001_001001_00180018_09001 | 17221 | 0.01216 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:fixed_gen,owner:20640,power:0.0122,file:NaN,cos_phi:0.99
234 | 7091091_001001_001001_00180018_09001 | 17221 | 0.01216 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:wind,owner:20640,power:0.0122,file:NaN,cos_phi:0.99,height:30
236 | 7091091_001001_001001_00140014_09001 | 17221 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:battery,owner:20640,power:0.16,file:NaN,cos_phi:0.99,capacity:0.192,efficiency:0.95,soc:0.5,g2b:False,b2g:False
1000 | 7091091_001001_001001_00180018_09001 | 13014 | 0.01216 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:fixed_gen,owner:20644,power:0.0122,file:NaN,cos_phi:0.99
1001 | 7091091_001001_001001_00180018_09001 | 13014 | 0.01216 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:wind,owner:20644,power:0.0122,file:NaN,cos_phi:0.99,height:30
1002 | 7091091_001001_001001_00140014_09001 | 13014 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:battery,owner:20644,power:0.16,file:NaN,cos_phi:0.99,capacity:0.192,efficiency:0.95,soc:0.5,g2b:False,b2g:False
1003 | 7091091_001001_001001_00710071_09001 | 13014 | 0.009 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:pv,owner:20644,power:0.009,file:NaN,cos_phi:0.99,orientation:11,angle:33
1004 | 7091091_001001_001001_00020004_09001 | 16517 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:heat_storage,owner:25007,power:0.16,capacity:0.192,efficiency:0.95,soc:0.5
1005 | 7091091_001001_001001_00020004_09002 | 16517 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:wind,owner:25007,power:0.16,file:NaN,cos_phi:0.99,height:30
1006 | 7091091_001001_001001_00020004_09003 | 16517 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:fixed_gen,owner:25007,power:0.16,file:NaN,cos_phi:0.99
1007 | 7091091_001001_001001_00020004_09001 | 19889 | 0.16 | 0 | 1 | 0.001 | TRUE |  | TRUE | plant_type:heat_storage,owner:20683,power:0.16,capacity:0.192,efficiency:0.95,soc:0.5

## switch
| bus | element | et | type | closed | name | z_ohm
106 | 21623 | 23153 | l | CB | TRUE |  | 0
107 | 21767 | 23157 | l | CB | FALSE |  | 0
382 | 21943 | 24730 | l | CB | TRUE |  | 0
383 | 21623 | 24734 | l | CB | FALSE |  | 0
626 | 21767 | 26156 | l | CB | TRUE |  | 0
627 | 21610 | 26160 | l | CB | TRUE |  | 0
1140 | 21623 | 28944 | l | CB | TRUE |  | 0
1153 | 21623 | 29067 | l | CB | TRUE |  | 0
1154 | 21767 | 29074 | l | CB | TRUE |  | 0
1602 | 21943 | 31357 | l | CB | TRUE |  | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max | r0x0_max | x0x_max | r0x0_min | x0x_min | description
0 | 3091091_000022 | 22165 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km | alpha | temperature_degree_celsius | description | line_idx | folder_id | section_idx
13166 | 7091091_001001_001001_00240025_06001 | NAYY-J 4x50 | 22836 | 22837 | 0.012 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 13166 | SWF | 0
13407 | 7091091_001001_001001_00670068_06001 | NYY-J 4x35 | 23081 | 13888 | 0.101 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13407 | SWF | 0
13458 | 7091091_001001_001001_00220023_06001 | NAYY-J 4x50 | 23128 | 23129 | 0.017 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 13458 | SWF | 0
13585 | 7091091_001001_001001_00060016_06001 | NYY-J 4x35 | 23256 | 20588 | 0.017 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13585 | SWF | 0
13798 | 7091091_001001_001001_00080017_06001 | NAYY-J 4x50 | 23463 | 21623 | 0.027 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 13798 | SWF | 0
14093 | 7091091_001001_001001_00350036_06001 | NAYY-J 4x50 | 23763 | 23764 | 0.077 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 14093 | SWF | 0
14208 | 7091091_001001_001001_00080018_06002 | NYY-J 3x150SM 0.6/1kV | 23873 | 17221 | 0.015 | 0.1255 | 0.073199 | 1320.0001 | 0 | 0.426 | 1 | 1 | cs | TRUE | 0.5021 | 0.2928 | 588.1 | 0.00393 | 70 |  | 14208 | SWF | 0
14391 | 7091091_001001_001001_00210028_06001 | NAYY-J 4x50 | 24051 | 24052 | 0.017 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 14391 | SWF | 0
14534 | 7091091_001001_001001_00290030_06001 | NAYY-J 4x50 | 24189 | 24190 | 0.015 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 14534 | SWF | 0
14838 | 7091091_001001_001001_00430046_06001 | NAYY-J 4x50 | 24489 | 14787 | 0.018 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 14838 | SWF | 0
15088 | 7091091_001001_001001_00100011_06001 | NYY-J 4x50 | 24723 | 13014 | 0.015 | 0.38696 | 0.084823 | 0 | 0 | 0.185 | 1 | 1 | cs | TRUE | 1.5478 | 0.33929 | 0 | 0.00393 | 70 |  | 15088 | SWF | 0
15362 | 7091091_001001_001001_00470048_06001 | NAYY-J 4x50 | 24978 | 24979 | 0.008 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 15362 | SWF | 0
15371 | 7091091_001001_001001_00050014_06001 | NYY-J 4x35 | 24987 | 24988 | 0.026 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15371 | SWF | 0
15372 | 7091091_001001_001001_00050014_06002 | NYY-J 4x35 | 24988 | 19889 | 0.005 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15372 | SWF | 0
15584 | 7091091_001001_001001_00370038_06002 | NYY-J 4x50 | 25191 | 17087 | 0.028 | 0.38696 | 0.084823 | 0 | 0 | 0.185 | 1 | 1 | cs | TRUE | 1.5478 | 0.33929 | 0 | 0.00393 | 70 |  | 15584 | SWF | 0
15831 | 7091091_001001_001001_00440056_06001 | NAYY-J 4x50 | 25422 | 17261 | 0.019 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 15831 | SWF | 0
15924 | 7091091_001001_001001_00590060_06001 | NAYY-J 4x50 | 13076 | 25512 | 0.009 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 15924 | SWF | 0
16204 | 7091091_001001_001001_00510052_06001 | NAYY-J 4x50 | 25791 | 20680 | 0.015 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 16204 | SWF | 0
16356 | 7091091_001001_001001_00370038_06001 | NAYY-J 4x50 | 25929 | 25191 | 0.015 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 16356 | SWF | 0
16875 | 7091091_001001_001001_00330034_06001 | NAYY-J 4x50 | 26400 | 26401 | 0.007 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 16875 | SWF | 0
17004 | 7091091_001001_001001_00410042_06001 | NYY-J 4x35 | 21767 | 26522 | 0.009 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17004 | SWF | 0
17286 | 7091091_001001_001001_00570058_06001 | NAYY-J 4x50 | 26773 | 26774 | 0.005 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 17286 | SWF | 0
17909 | 7091091_001001_001001_00310032_06001 | NAYY-J 4x50 | 27337 | 27338 | 0.017 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 17909 | SWF | 0
18060 | 7091091_001001_001001_00690071_06002 | NYY-J 4x35 | 27474 | 20267 | 0.03 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18060 | SWF | 0
18467 | 7091091_001001_001001_00020003_06001 | NYY 4x10 | 21943 | 18229 | 0.004 | 1.8303 | 0.094562 | 0 | 0 | 0.075 | 1 | 1 | cs | TRUE | 7.3214 | 0.37825 | 0 | 0.00393 | 70 |  | 18467 | SWF | 0
18664 | 7091091_001001_001001_00080018_06001 | NAYY 4x185SE 0.6/1kV | 21623 | 23873 | 0.015 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 18664 | SWF | 0
18805 | 7091091_001001_001001_00080019_06001 | NAYY 4x95SE 0.6/1kV | 21623 | 16503 | 0.083 | 0.3208 | 0.081996 | 770 | 0 | 0.211 | 1 | 1 | cs | TRUE | 1.2833 | 0.32798 | 349.2 | 0.00403 | 70 |  | 18805 | SWF | 0
18824 | 7091091_001001_001001_00650066_06001 | NYY-J 4x35 | 28155 | 14505 | 0.018 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18824 | SWF | 0
19307 | 7091091_001001_001001_00350036_06002 | NAYY-J 4x50 | 23764 | 20128 | 0.013 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 19307 | SWF | 0
19345 | 7091091_001001_001001_00120013_06001 | NYY-J 4x35 | 28578 | 18894 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19345 | SWF | 0
19442 | 7091091_001001_001001_00570058_06002 | NYY-J 4x35 | 26774 | 20423 | 0.036 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19442 | SWF | 0
19658 | 7091091_001001_001001_00390040_06001 | NAYY-J 4x50 | 28854 | 13174 | 0.033 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 19658 | SWF | 0
20106 | 7091091_001001_001001_00260027_06001 | NAYY-J 4x50 | 29243 | 14739 | 0.017 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 20106 | SWF | 0
20467 | 7091091_001001_001001_00490050_06001 | NAYY-J 4x50 | 29550 | 13846 | 0.009 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 20467 | SWF | 0
21070 | 7091091_001001_001001_00020004_06002 | NYY-J 4x50 | 30059 | 16517 | 0.05 | 0.38696 | 0.084823 | 0 | 0 | 0.185 | 1 | 1 | cs | TRUE | 1.5478 | 0.33929 | 0 | 0.00393 | 70 |  | 21070 | SWF | 0
21106 | 7091091_001001_001001_00020004_06001 | NYY-J 3x150SM 0.6/1kV | 21943 | 16517 | 0.135 | 0.1255 | 0.073199 | 1320.0001 | 0 | 0.426 | 1 | 1 | cs | TRUE | 0.5021 | 0.2928 | 588.1 | 0.00393 | 70 |  | 21106 | SWF | 0
21166 | 7091091_001001_001001_00630064_06001 | NYY-J 4x35 | 30136 | 17155 | 0.02 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 21166 | SWF | 0
21469 | 7091091_001001_001001_00450062_06001 | NAYY-J 4x50 | 30390 | 16582 | 0.007 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 21469 | SWF | 0
21883 | 7091091_001001_001001_00050015_06001 | NYY-J 3x70SM 0.6/1kV | 24987 | 17868 | 0.073 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 21883 | SWF | 0
22243 | 7091091_001001_001001_00690070_06001 | NYY-J 4x35 | 30999 | 14786 | 0.006 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22243 | SWF | 0
22413 | 7091091_001001_001001_00530054_06001 | NYY-J 4x35 | 21610 | 20652 | 0.028 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22413 | SWF | 0
22613 | 7091091_001001_001001_00530055_06001 | NYY-J 4x35 | 21610 | 14854 | 0.029 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22613 | SWF | 0
23153 | 7091091_001001_001001_00080017_06305 | NAYY 4x185SE 0.6/1kV | 21623 | 23463 | 0.014 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 23153 | SWF | 0
23154 | 7091091_001001_001001_00170022_06001 | NAYY 4x185SE 0.6/1kV | 23463 | 23128 | 0.044 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 23154 | SWF | 0
23155 | 7091091_001001_001001_00220024_06001 | NAYY 4x185SE 0.6/1kV | 23128 | 22836 | 0.036 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 23155 | SWF | 0
23156 | 7091091_001001_001001_00240026_06001 | NAYY 4x185SE 0.6/1kV | 22836 | 29243 | 0.022 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 23156 | SWF | 0
23157 | 7091091_001001_001001_00260041_06001 | NAYY 4x185SE 0.6/1kV | 29243 | 21767 | 0.065 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 23157 | SWF | 0
24303 | 7091091_001001_001001_00020005_06001 | NYY-J 3x70SM 0.6/1kV | 21943 | 24987 | 0.031 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 24303 | SWF | 0
24730 | 7091091_001001_001001_00020006_06001 | NAYY 4x150SE 0.6/1kV | 21943 | 23256 | 0.06 | 0.2067 | 0.080425 | 830 | 0 | 0.27 | 1 | 1 | cs | TRUE | 0.8267 | 0.3217 | 385.9 | 0.00403 | 70 |  | 24730 | SWF | 0
24731 | 7091091_001001_001001_00040006_06001 | NAYY 4x150SE 0.6/1kV | 23256 | 30059 | 0.029 | 0.2067 | 0.080425 | 830 | 0 | 0.27 | 1 | 1 | cs | TRUE | 0.8267 | 0.3217 | 385.9 | 0.00403 | 70 |  | 24731 | SWF | 0
24732 | 7091091_001001_001001_00040010_06001 | NAYY 4x150SE 0.6/1kV | 30059 | 24723 | 0.047 | 0.2067 | 0.080425 | 830 | 0 | 0.27 | 1 | 1 | cs | TRUE | 0.8267 | 0.3217 | 385.9 | 0.00403 | 70 |  | 24732 | SWF | 0
24733 | 7091091_001001_001001_00100012_06001 | NAYY 4x150SE 0.6/1kV | 24723 | 28578 | 0.046 | 0.2067 | 0.080425 | 830 | 0 | 0.27 | 1 | 1 | cs | TRUE | 0.8267 | 0.3217 | 385.9 | 0.00403 | 70 |  | 24733 | SWF | 0
24734 | 7091091_001001_001001_00120008_06001 | NAYY 4x150SE 0.6/1kV | 28578 | 21623 | 0.039 | 0.2067 | 0.080425 | 830 | 0 | 0.27 | 1 | 1 | cs | TRUE | 0.8267 | 0.3217 | 385.9 | 0.00403 | 70 |  | 24734 | SWF | 0
26156 | 7091091_001001_001001_00410043_06001 | NAYY 4x185SE 0.6/1kV | 21767 | 24489 | 0.015 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 26156 | SWF | 0
26157 | 7091091_001001_001001_00430047_06001 | NAYY 4x185SE 0.6/1kV | 24489 | 24978 | 0.031 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 26157 | SWF | 0
26158 | 7091091_001001_001001_00470049_06001 | NAYY 4x185SE 0.6/1kV | 24978 | 29550 | 0.031 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 26158 | SWF | 0
26159 | 7091091_001001_001001_00490051_06001 | NAYY 4x185SE 0.6/1kV | 29550 | 25791 | 0.034 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 26159 | SWF | 0
26160 | 7091091_001001_001001_00510053_06001 | NAYY 4x185SE 0.6/1kV | 25791 | 21610 | 0.006 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 26160 | SWF | 0
26873 | 7091091_001001_001001_00010002_06002 | NYY-O 3x240SM 0.6/1kV | 21943 | 32722 | 0.001 | 0.0777 | 0.072571 | 1390 | 0 | 0.458 | 1 | 1 | cs | TRUE | 0.3106 | 0.29028 | 643.2 | 0.00393 | 70 |  | 26873 | SWF | 0
28944 | 7091091_001001_001001_00020008_06002 | NAYY 4x185SE 0.6/1kV | 33146 | 21623 | 0.016 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28944 | SWF | 0
29067 | 7091091_001001_001001_00080021_06001 | NAYY 4x185SE 0.6/1kV | 21623 | 24052 | 0.038 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29067 | SWF | 0
29068 | 7091091_001001_001001_00210029_06001 | NAYY 4x185SE 0.6/1kV | 24052 | 24190 | 0.001 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29068 | SWF | 0
29069 | 7091091_001001_001001_00290031_06001 | NAYY 4x185SE 0.6/1kV | 24190 | 27337 | 0.014 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29069 | SWF | 0
29070 | 7091091_001001_001001_00310033_06001 | NAYY 4x185SE 0.6/1kV | 27337 | 26400 | 0.03 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29070 | SWF | 0
29071 | 7091091_001001_001001_00330035_06001 | NAYY 4x185SE 0.6/1kV | 26400 | 23763 | 0.001 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29071 | SWF | 0
29072 | 7091091_001001_001001_00350037_06001 | NAYY 4x185SE 0.6/1kV | 23763 | 25929 | 0.001 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29072 | SWF | 0
29073 | 7091091_001001_001001_00370039_06001 | NAYY 4x185SE 0.6/1kV | 25929 | 28854 | 0.03 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29073 | SWF | 0
29074 | 7091091_001001_001001_00390041_06001 | NAYY 4x185SE 0.6/1kV | 28854 | 21767 | 0.065 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 29074 | SWF | 0
30639 | 7091091_001001_001001_00410044_06001 | NAYY 4x185SE 0.6/1kV | 21767 | 25422 | 0.047 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30639 | SWF | 0
30640 | 7091091_001001_001001_00440057_06001 | NAYY 4x185SE 0.6/1kV | 25422 | 26773 | 0.001 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30640 | SWF | 0
30641 | 7091091_001001_001001_00570059_06001 | NAYY 4x185SE 0.6/1kV | 26773 | 25512 | 0.009 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30641 | SWF | 0
30642 | 7091091_001001_001001_00590061_06001 | NAYY 4x185SE 0.6/1kV | 25512 | 33442 | 0.004 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30642 | SWF | 0
31104 | 7091091_001001_001001_00020007_06001 | NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 21943 | 19705 | 0.003 | 1.8769 | 0.35 | 11 | 0 | 0.105 | 1 | 1 | ol | TRUE | 0 | 0 | 0 | 0.00403 | 90 |  | 31104 | SWF | 0
31357 | 7091091_001001_001001_00020008_06001 | NYY-J 3x150SM 0.6/1kV | 21943 | 33146 | 0.206 | 0.1255 | 0.073199 | 1320.0001 | 0 | 0.426 | 1 | 1 | cs | TRUE | 0.5021 | 0.2928 | 588.1 | 0.00393 | 70 |  | 31357 | SWF | 0
31779 | 7091091_001001_001001_00410045_06001 | NYY-J 3x70SM 0.6/1kV | 21767 | 30390 | 0.064 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31779 | SWF | 0
31780 | 7091091_001001_001001_00450063_06001 | NYY-J 3x70SM 0.6/1kV | 30390 | 30136 | 0.021 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31780 | SWF | 0
31781 | 7091091_001001_001001_00630065_06001 | NYY-J 3x70SM 0.6/1kV | 30136 | 28155 | 0.008 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31781 | SWF | 0
31782 | 7091091_001001_001001_00650067_06001 | NYY-J 3x70SM 0.6/1kV | 28155 | 23081 | 0.036 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31782 | SWF | 0
31783 | 7091091_001001_001001_00670069_06001 | NYY-J 3x70SM 0.6/1kV | 23081 | 30999 | 0.001 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31783 | SWF | 0
31784 | 7091091_001001_001001_00690071_06001 | NYY-J 3x70SM 0.6/1kV | 30999 | 27474 | 0.002 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31784 | SWF | 0
33801 | 7091091_001001_001001_00010002_06001 | NS-Leitungstyp_fiktiv | 32722 | 22166 | 0.002 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 33801 | SWF | 0

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_set_vm_pu | description | equipment
22 | 6091091_000000_000000_00000000_05001 | MSNS_0063 | 22165 | 22166 | 0.4 | 20 | 0.4 | 3.81 | 0.9605 | 0.397 | 0.3 | 150 | [6 empty] | 0 | FALSE | 1 | 1 | TRUE | 3 | 0 | 100 | 0 | 0.9 | 1

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
13166 | 650980.6355 | 5511238.7055 | 650980.9471 | 5511238.9942 | 650981.0715 | 5511239.1681 | 650980.7604 | 5511240.2252 | 650980.574 | 5511240.8921 | 650980.7169 | 5511245.5894 | 650980.8476 | 5511249.8861 | 650980.8523 | 5511250.0886 | 650980.9221 | 5511250.1801 | 650981.0932 | 5511250.1757
13407 | 651084.5902 | 5511178.6236 | 651084.6798 | 5511178.4518 | 651086.8525 | 5511178.0939 | 651087.0802 | 5511178.153 | 651092.1235 | 5511178.6499 | 651094.6443 | 5511178.8544 | 651094.7292 | 5511178.5272 | 651096.1894 | 5511127.4903 | 651096.2777 | 5511107.0042 | 651096.278 | 5511106.9787 | 651096.3052 | 5511105.3728 | 651095.0379 | 5511104.1856 | 651094.4426 | 5511103.6691 | 651091.6533 | 5511103.1148 | 651082.665 | 5511102.6046 | 651082.3359 | 5511102.3726 | 651082.0277 | 5511101.9187 | 651081.9483 | 5511101.3836 | 651081.9331 | 5511101.0049 | 651081.893 | 5511100.0057
13458 | 650945.3812 | 5511243.9627 | 650945.6728 | 5511244.0492 | 650947.5746 | 5511243.9518 | 650947.9768 | 5511244.1754 | 650948.0202 | 5511244.9742 | 650948.6844 | 5511257.2006 | 650948.533 | 5511257.7825 | 650948.0102 | 5511257.8372
13585 | 650728.7304 | 5511259.4775 | 650728.3539 | 5511259.8654 | 650721.3347 | 5511273.2177 | 650721.2497 | 5511273.9475 | 650721.1341 | 5511274.9408
13798 | 650901.4171 | 5511247.9946 | 650901.7811 | 5511247.8471 | 650901.9769 | 5511247.5642 | 650901.7696 | 5511247.1883 | 650901.3388 | 5511247.2011 | 650901.1442 | 5511247.3134 | 650901.0091 | 5511247.6881 | 650901.0099 | 5511247.9182 | 650900.9902 | 5511256.9213 | 650900.9843 | 5511257.3212 | 650900.9623 | 5511257.3703 | 650900.709 | 5511257.381
14093 | 650970.997 | 5511241.1554 | 650972.5913 | 5511240.6369 | 650972.8313 | 5511239.9704 | 650976.4993 | 5511237.074 | 650976.5797 | 5511236.3501 | 650976.0687 | 5511228.1664 | 650975.8173 | 5511227.1678 | 650975.7314 | 5511225.6829 | 650976.341 | 5511199.1028 | 650976.1864 | 5511177.6333 | 650976.0789 | 5511168.0865 | 650976.0472 | 5511167.4971
14208 | 650874.2593 | 5511250.3849 | 650873.584 | 5511250.0186 | 650873.2782 | 5511248.9722 | 650872.4988 | 5511236.9992 | 650872.4339 | 5511236.0013
14391 | 650922.0127 | 5511231.4773 | 650922.0933 | 5511231.4833 | 650922.6364 | 5511231.7458 | 650922.7413 | 5511232.1837 | 650922.6607 | 5511238.3112 | 650922.5969 | 5511240.3002 | 650924.9411 | 5511245.1074 | 650924.8869 | 5511245.6633 | 650925.1589 | 5511245.7637 | 650925.4385 | 5511245.5247 | 650925.2675 | 5511245.2516 | 650924.7089 | 5511245.2557
14534 | 650922.9211 | 5511231.5769 | 650922.9226 | 5511231.5867 | 650922.8412 | 5511232.1839 | 650922.7101 | 5511239.6833 | 650922.7006 | 5511240.1733 | 650925.0673 | 5511245.0498 | 650925.1742 | 5511245.4058 | 650925.3846 | 5511245.6226 | 650925.6609 | 5511245.54 | 650925.9016 | 5511245.1257
14838 | 651050.5887 | 5511266.9398 | 651050.7368 | 5511266.8819 | 651050.7205 | 5511266.7432 | 651050.5185 | 5511266.6831 | 651050.3661 | 5511266.8001 | 651050.1228 | 5511267.4059 | 651053.4917 | 5511274.0495 | 651053.7531 | 5511276.4685 | 651053.3561 | 5511281.6245 | 651053.3266 | 5511282.1235 | 651053.2677 | 5511283.1218
15088 | 650804.5672 | 5511257.9437 | 650804.5265 | 5511257.4924 | 650804.0631 | 5511252.3482 | 650803.2809 | 5511243.6667 | 650803.1912 | 5511242.6708
15362 | 651034.7739 | 5511291.491 | 651034.7615 | 5511291.0502 | 651034.6364 | 5511290.9252 | 651034.4426 | 5511291.0175 | 651034.3635 | 5511291.2445 | 651034.1969 | 5511291.408 | 651034.016 | 5511291.3973 | 651032.6298 | 5511291.3055 | 651031.1321 | 5511291.2157 | 651028.5936 | 5511291.0492 | 651028.3048 | 5511291.7462
15371 | 650653.6074 | 5511231.7213 | 650653.6545 | 5511230.805 | 650654.1024 | 5511223.8599 | 650655.0485 | 5511214.862 | 650656.7669 | 5511206.0013
15372 | 650657.1162 | 5511204.0703 | 650655.0684 | 5511203.7909 | 650654.8379 | 5511203.7594 | 650653.8471 | 5511203.6242
15584 | 650975.6047 | 5511227.4796 | 650975.6595 | 5511227.3617 | 650975.6414 | 5511226.06 | 650975.5798 | 5511225.5972 | 650974.832 | 5511215.5123 | 650974.2902 | 5511209.6797 | 650974.4861 | 5511209.4115 | 650975.6695 | 5511209.213 | 650977.0264 | 5511209.2673 | 650981.3679 | 5511211.8955 | 650982.6116 | 5511211.9115 | 650983.6115 | 5511211.9244
15831 | 651102.0634 | 5511259.6872 | 651102.1185 | 5511259.8637 | 651101.9829 | 5511260.1248 | 651102.1832 | 5511260.3728 | 651102.4991 | 5511260.3728 | 651102.6094 | 5511260.1201 | 651102.4065 | 5511259.9346 | 651102.1704 | 5511259.9142 | 651101.7599 | 5511260.7115 | 651101.1248 | 5511262.1956 | 651101.2233 | 5511264.1942 | 651101.282 | 5511265.3846 | 651101.9295 | 5511274.6795 | 651100.9304 | 5511274.7174 | 651099.9311 | 5511274.7553
15924 | 651112.0759 | 5511269.7222 | 651112.0266 | 5511268.7234 | 651111.8295 | 5511264.7292 | 651111.6189 | 5511260.4592 | 651111.474 | 5511260.3317
16204 | 651033.4693 | 5511356.0998 | 651033.5612 | 5511355.3495 | 651034.4215 | 5511355.1072 | 651035.5203 | 5511355.0911 | 651038.7494 | 5511354.8901 | 651041.7184 | 5511354.939 | 651043.7599 | 5511354.9306 | 651044.9245 | 5511355.0201 | 651045.8784 | 5511355.0133 | 651045.868 | 5511353.9134 | 651045.8586 | 5511352.9134
16356 | 650972.2539 | 5511241.0388 | 650972.6935 | 5511239.8244 | 650976.3272 | 5511236.9551 | 650976.3801 | 5511236.3626 | 650975.8692 | 5511228.1789 | 650975.6047 | 5511227.4796
16875 | 650969.6336 | 5511241.2819 | 650969.2504 | 5511241.217 | 650969.0973 | 5511241.1213 | 650969.4952 | 5511235.6096 | 650969.6086 | 5511235.4333 | 650969.865 | 5511235.3935 | 650969.9035 | 5511235.2576
17004 | 651058.6374 | 5511257.4739 | 651059.0781 | 5511257.4259 | 651057.4703 | 5511253.9088 | 651057.752 | 5511252.4266 | 651057.328 | 5511251.7157 | 651056.2396 | 5511251.7527 | 651055.7733 | 5511251.9537 | 651055.729 | 5511252.2624
17286 | 651102.967 | 5511259.7223 | 651102.5837 | 5511259.8248 | 651102.1464 | 5511260.1216 | 651102.1806 | 5511260.4371 | 651102.5241 | 5511260.4508 | 651102.6288 | 5511260.2144 | 651102.3565 | 5511260.0877 | 651101.37 | 5511262.3802
17909 | 650939.7203 | 5511243.6192 | 650939.283 | 5511243.5382 | 650937.8352 | 5511239.7134 | 650938.1674 | 5511229.0077 | 650938.1616 | 5511228.4793 | 650938.3024 | 5511228.2941 | 650938.8679 | 5511228.2721
18060 | 651081.9973 | 5511178.6599 | 651081.8201 | 5511178.6245 | 651080.5965 | 5511177.9722 | 651079.1778 | 5511177.8355 | 651072.8198 | 5511177.2111 | 651069.2473 | 5511176.8234 | 651067.5482 | 5511165.8059 | 651067.4903 | 5511163.1178 | 651065.6892 | 5511163.1563 | 651064.6895 | 5511163.1777
18467 | 650667.8133 | 5511253.3768 | 650667.4508 | 5511253.0393
18664 | 650888.1133 | 5511250.3202 | 650888.0986 | 5511249.5041 | 650887.927 | 5511249.1229 | 650887.2069 | 5511248.9977 | 650876.5243 | 5511249.9238 | 650875.0427 | 5511250.1977 | 650874.5092 | 5511250.3973 | 650874.2593 | 5511250.3849
18805 | 650888.4031 | 5511250.2956 | 650888.4866 | 5511248.9903 | 650890.5421 | 5511248.7983 | 650901.4013 | 5511247.8956 | 650924.7596 | 5511245.7567 | 650939.755 | 5511244.1447 | 650946.4503 | 5511243.7196 | 650947.401 | 5511243.6888 | 650948.1311 | 5511244.0597 | 650948.22 | 5511244.968 | 650948.976 | 5511258.8827 | 650949.2243 | 5511261.9664 | 650950.0097 | 5511262.7359 | 650951.4511 | 5511262.6368 | 650952.4488 | 5511262.5683
18824 | 651098.0091 | 5511202.9083 | 651093.9177 | 5511203.2557 | 651088.5443 | 5511203.7261 | 651083.1319 | 5511204.1409 | 651083.1586 | 5511201.7906 | 651083.17 | 5511200.7906
19307 | 650976.0472 | 5511167.4971 | 650986.62 | 5511167.1099 | 650986.75 | 5511165.5158 | 650986.8313 | 5511164.5191
19345 | 650850.3108 | 5511253.4495 | 650850.5778 | 5511255.3816 | 650850.7147 | 5511256.3722
19442 | 651101.37 | 5511262.3802 | 651101.4975 | 5511264.1833 | 651102.43 | 5511277.364 | 651105.3863 | 5511288.4441 | 651105.8077 | 5511290.4698 | 651106.3866 | 5511293.275 | 651106.3318 | 5511293.4206 | 651106.1736 | 5511293.4906 | 651103.0761 | 5511293.6043 | 651102.0768 | 5511293.641
19658 | 651001.8532 | 5511241.2838 | 651001.1057 | 5511241.0983 | 651001.6332 | 5511239.0503 | 651002.0937 | 5511238.995 | 651002.5271 | 5511238.9914 | 651019.8574 | 5511242.1987 | 651021.4459 | 5511233.1871 | 651022.6275 | 5511233.3962 | 651023.6122 | 5511233.5706
20106 | 651001.8393 | 5511241.7901 | 651001.2775 | 5511241.7415 | 651001.2271 | 5511241.7922 | 651000.5326 | 5511256.9104 | 651000.4867 | 5511257.9094
20467 | 651033.7358 | 5511322.1619 | 651033.5261 | 5511321.4587 | 651033.4286 | 5511321.3947 | 651033.1497 | 5511321.6138 | 651032.6352 | 5511321.7234 | 651028.876 | 5511321.9241 | 651027.2896 | 5511322.0712 | 651025.9817 | 5511322.0091 | 651025.5047 | 5511321.9301
21070 | 650757.2426 | 5511259.7987 | 650757.2226 | 5511259.329 | 650756.8703 | 5511251.0536 | 650756.8532 | 5511250.6524 | 650757.1751 | 5511250.0921 | 650757.5414 | 5511249.5029 | 650759.8815 | 5511238.4346 | 650760.2224 | 5511235.9695 | 650758.2563 | 5511218.9664 | 650758.2967 | 5511211.3363 | 650758.3262 | 5511210.8268
21106 | 650671.4181 | 5511253.8777 | 650672.4673 | 5511252.7575 | 650675.0893 | 5511250.1478 | 650675.7122 | 5511249.5278 | 650684.9448 | 5511252.1425 | 650691.5368 | 5511253.7006 | 650695.5571 | 5511254.6469 | 650718.0297 | 5511258.6017 | 650718.0651 | 5511258.4936 | 650720.1707 | 5511252.0634 | 650720.6873 | 5511250.4856 | 650720.9808 | 5511250.3125 | 650724.1736 | 5511250.9728 | 650755.4322 | 5511250.6271 | 650756.6496 | 5511250.5061 | 650757.0906 | 5511250.0387 | 650757.4245 | 5511249.5015 | 650759.7844 | 5511238.4066 | 650760.1183 | 5511235.992 | 650758.1564 | 5511218.9508 | 650758.1967 | 5511211.3325 | 650758.1464 | 5511210.8347
21166 | 651098.2705 | 5511210.6511 | 651092.0232 | 5511210.9988 | 651090.4153 | 5511210.6738 | 651080.4632 | 5511211.0962 | 651080.2957 | 5511211.2389 | 651080.3098 | 5511211.7447 | 651080.3375 | 5511212.7443
21469 | 651099.1658 | 5511231.3171 | 651098.8013 | 5511231.4225 | 651094.7386 | 5511231.6591 | 651093.6579 | 5511231.942 | 651092.6905 | 5511232.1951
21883 | 650653.6074 | 5511231.7213 | 650600.3731 | 5511201.0294 | 650603.6312 | 5511194.7221 | 650601.323 | 5511193.5286 | 650601.5098 | 5511193.1669 | 650601.9688 | 5511192.2785
22243 | 651083.7111 | 5511178.5884 | 651083.6974 | 5511178.2676 | 651082.1135 | 5511177.5041 | 651082.2447 | 5511174.4595 | 651082.2877 | 5511173.4604
22413 | 651034.2846 | 5511361.641 | 651034.1632 | 5511361.6466 | 651034.1444 | 5511362.0248 | 651033.9166 | 5511366.5879 | 651034.7312 | 5511372.5856 | 651035.056 | 5511373.7764 | 651035.3769 | 5511374.0741 | 651035.748 | 5511374.1712 | 651042.5454 | 5511373.9929 | 651048.541 | 5511373.7224 | 651048.6856 | 5511372.4211 | 651048.796 | 5511371.4272
22613 | 651034.2841 | 5511361.541 | 651034.0622 | 5511361.5477 | 651034.0392 | 5511362.0197 | 651033.8166 | 5511366.5876 | 651033.8768 | 5511370.4631 | 651033.0981 | 5511370.5719 | 651030.4913 | 5511370.6259 | 651024.3267 | 5511370.7534 | 651016.6292 | 5511370.8811 | 651016.6094 | 5511369.9151 | 651016.589 | 5511368.9153
23153 | 650888.3038 | 5511250.3041 | 650888.336 | 5511249.3948 | 650890.6639 | 5511248.8885 | 650901.4171 | 5511247.9946
23154 | 650924.7727 | 5511245.8559 | 650939.7586 | 5511244.2448 | 650945.3812 | 5511243.9627
23155 | 650949.0321 | 5511243.5198 | 650961.4145 | 5511242.5909 | 650972.6287 | 5511241.5592 | 650980.6355 | 5511238.7055
23156 | 650981.2185 | 5511238.4891 | 650995.751 | 5511240.6113 | 651000.2172 | 5511241.4775 | 651001.2307 | 5511241.6677 | 651001.8393 | 5511241.7901
23157 | 651018.4697 | 5511244.9917 | 651031.3168 | 5511247.5561 | 651034.8806 | 5511248.331 | 651035.7284 | 5511248.7307 | 651043.8488 | 5511255.7803 | 651047.0732 | 5511258.5808 | 651048.8574 | 5511259.4913 | 651050.4251 | 5511259.9774 | 651056.5276 | 5511259.5245 | 651057.1919 | 5511259.4863 | 651057.9958 | 5511259.3984 | 651058.7494 | 5511259.5687 | 651059.3576 | 5511259.623 | 651059.5913 | 5511259.2821 | 651059.4873 | 5511257.8769 | 651059.0783 | 5511257.6886 | 651058.6585 | 5511257.723
24303 | 650671.277 | 5511253.736 | 650671.4726 | 5511253.3065 | 650670.0733 | 5511251.9322 | 650669.9376 | 5511251.7406 | 650668.8614 | 5511248.1956 | 650668.2383 | 5511242.2676 | 650656.0508 | 5511235.4414 | 650655.2166 | 5511234.4337 | 650654.3655 | 5511232.9505 | 650653.6074 | 5511231.7213
24730 | 650671.3475 | 5511253.8068 | 650672.8506 | 5511253.1725 | 650677.1458 | 5511249.1378 | 650682.8448 | 5511250.7924 | 650691.8346 | 5511253.1805 | 650695.6135 | 5511254.1179 | 650709.9019 | 5511256.6361 | 650723.7823 | 5511259.3328 | 650728.7304 | 5511259.4775
24731 | 650747.2854 | 5511260.0148 | 650757.2426 | 5511259.7987
24732 | 650772.4549 | 5511259.4645 | 650783.5068 | 5511259.4079 | 650792.4734 | 5511259.1527 | 650804.5672 | 5511257.9437
24733 | 650835.1834 | 5511255.4559 | 650847.5949 | 5511253.9091 | 650850.3108 | 5511253.4495
24734 | 650850.5591 | 5511253.4074 | 650862.0457 | 5511252.3816 | 650873.3788 | 5511251.6014 | 650887.8736 | 5511249.7486 | 650887.9224 | 5511250.3364
26156 | 651058.6501 | 5511257.6233 | 651059.2777 | 5511257.5662 | 651059.4473 | 5511258.1255 | 651059.5309 | 5511258.7894 | 651059.185 | 5511259.6862 | 651058.4581 | 5511259.5971 | 651057.2782 | 5511259.5799 | 651056.5955 | 5511259.9187 | 651055.168 | 5511260.0264 | 651051.8246 | 5511266.0966 | 651050.5887 | 5511266.9398
26157 | 651045.072 | 5511270.9026 | 651042.203 | 5511273.7751 | 651038.3308 | 5511277.9681 | 651037.5871 | 5511278.855 | 651036.8942 | 5511279.9967 | 651036.2018 | 5511281.4177 | 651035.6989 | 5511283.2435 | 651034.7739 | 5511291.491
26158 | 651034.0583 | 5511304.914 | 651033.9274 | 5511308.6945 | 651033.7478 | 5511316.3915 | 651033.7358 | 5511322.1619
26159 | 651033.734 | 5511323.0303 | 651033.7142 | 5511332.4677 | 651033.3779 | 5511334.551 | 651033.4693 | 5511356.0998
26160 | 651033.4327 | 5511361.4524 | 651034.2835 | 5511361.441
26873 | 650671.0653 | 5511253.5234 | 650671.1172 | 5511253.465 | 650671.0281 | 5511253.3869 | 650670.7106 | 5511253.6958
28944 | 650873.3511 | 5511251.4689 | 650874.3512 | 5511251.3366 | 650874.5081 | 5511251.0487 | 650875.0502 | 5511250.5054 | 650876.5329 | 5511250.0234 | 650887.216 | 5511249.0972 | 650887.8879 | 5511249.2141 | 650888.0005 | 5511249.533 | 650888.0221 | 5511250.328
29067 | 650888.2045 | 5511250.3125 | 650888.2594 | 5511248.6427 | 650890.5955 | 5511248.253 | 650901.1963 | 5511247.4468 | 650924.7089 | 5511245.2557
29068 | 650925.9016 | 5511245.1257
29069 | 650939.7203 | 5511243.6192
29070 | 650945.4351 | 5511243.2752 | 650948.968 | 5511242.946 | 650969.6336 | 5511241.2819
29071 | 650970.997 | 5511241.1554
29072 | 650972.2539 | 5511241.0388
29073 | 650972.5525 | 5511241.0111 | 650981.1855 | 5511237.9374 | 650995.7409 | 5511240.1087 | 651000.8742 | 5511241.0957 | 651001.6499 | 5511241.2448 | 651001.8532 | 5511241.2838
29074 | 651018.5659 | 5511244.5011 | 651031.4147 | 5511247.0659 | 651035.0661 | 5511247.8656 | 651036.0168 | 5511248.319 | 651047.3715 | 5511258.1777 | 651049.018 | 5511259.1224 | 651050.471 | 5511259.5729 | 651056.4675 | 5511259.129 | 651057.3585 | 5511259.3229 | 651058.4573 | 5511259.3669 | 651059.4327 | 5511259.496 | 651059.3938 | 5511258.2134 | 651059.0271 | 5511257.7526 | 651058.6627 | 5511257.7728
30639 | 651058.6458 | 5511257.5735 | 651059.2656 | 5511257.5158 | 651059.3651 | 5511257.5449 | 651059.6512 | 5511257.6951 | 651066.6364 | 5511257.1776 | 651071.0681 | 5511256.8493 | 651073.8802 | 5511256.9418 | 651086.0972 | 5511257.0921 | 651088.0901 | 5511256.6683 | 651090.6197 | 5511255.7018 | 651092.6062 | 5511253.8514 | 651092.8736 | 5511253.7359 | 651093.1464 | 5511253.8555 | 651100.3858 | 5511259.6818 | 651101.313 | 5511259.7073 | 651101.6712 | 5511259.7316 | 651102.0634 | 5511259.6872
30640 | 651102.3036 | 5511259.6867 | 651102.967 | 5511259.7223
30641 | 651104.1492 | 5511259.7142 | 651111.474 | 5511260.3317
30642 | 651112.0502 | 5511260.3853 | 651112.2184 | 5511260.0221 | 651111.9614 | 5511259.7475 | 651111.4609 | 5511259.5949 | 651110.8872 | 5511259.7607 | 651110.9953 | 5511260.0291 | 651111.3466 | 5511260.0387
31104 | 650671.7708 | 5511254.2321 | 650671.3633 | 5511254.5955 | 650670.8062 | 5511254.7815 | 650669.8577 | 5511255.0981
31357 | 650671.2064 | 5511253.6651 | 650672.7094 | 5511253.031 | 650677.0921 | 5511248.914 | 650682.8851 | 5511250.5959 | 650691.8999 | 5511252.991 | 650695.6637 | 5511253.9237 | 650709.9951 | 5511256.3481 | 650723.8212 | 5511259.1431 | 650728.8142 | 5511259.2799 | 650747.3159 | 5511259.8156 | 650772.439 | 5511259.2648 | 650783.4998 | 5511259.208 | 650792.469 | 5511258.9528 | 650804.5637 | 5511257.7434 | 650812.2396 | 5511257.12 | 650835.1369 | 5511255.2591 | 650847.5736 | 5511253.7099 | 650850.5417 | 5511253.2076 | 650862.0036 | 5511252.1844 | 650873.3511 | 5511251.4689
31779 | 651058.6711 | 5511257.8724 | 651059.6648 | 5511257.7943 | 651066.6438 | 5511257.2773 | 651071.0701 | 5511256.9494 | 651073.878 | 5511257.0418 | 651086.1071 | 5511257.1922 | 651088.1186 | 5511256.7645 | 651090.6799 | 5511255.7858 | 651100.1624 | 5511252.4814 | 651100.4391 | 5511251.8884 | 651100.2006 | 5511251.0436 | 651099.6347 | 5511241.8765 | 651099.1658 | 5511231.3171
31780 | 651098.2087 | 5511211.703 | 651098.2705 | 5511210.6511
31781 | 651098.0091 | 5511202.9083
31782 | 651097.8358 | 5511185.943 | 651097.7746 | 5511179.9455 | 651097.7591 | 5511179.8778 | 651097.3412 | 5511179.586 | 651096.6809 | 5511179.4675 | 651092.4521 | 5511179.1082 | 651084.5902 | 5511178.6236
31783 | 651083.7111 | 5511178.5884
31784 | 651081.9973 | 5511178.6599
33801 | 650670.7106 | 5511253.6958 | 650668.5133 | 5511253.3143

## bus_geodata
| x | y | coords
14854 | 651016.589 | 5511368.9153
13846 | 651025.5047 | 5511321.9301
23081 | 651084.5902 | 5511178.6236
29243 | 651001.8393 | 5511241.7901
13888 | 651081.893 | 5511100.0057
23128 | 650945.3812 | 5511243.9627
23129 | 650948.0102 | 5511257.8372
25191 | 650975.6047 | 5511227.4796
21610 | 651034.4272 | 5511361.5156
20588 | 650721.1341 | 5511274.9408
21623 | 650888.1654 | 5511250.4103
16503 | 650952.4488 | 5511262.5683
24189 | 650922.9211 | 5511231.5769
24190 | 650925.9016 | 5511245.1257
16517 | 650758.2293 | 5511210.671
24723 | 650804.5672 | 5511257.9437
26773 | 651102.967 | 5511259.7223
22166 | 650668.5133 | 5511253.3143
26774 | 651101.37 | 5511262.3802
22165 | 650668.5133 | 5511254.3143
20128 | 650986.8313 | 5511164.5191
33442 | 651111.3466 | 5511260.0387
14505 | 651083.17 | 5511200.7906
20652 | 651048.796 | 5511371.4272
28854 | 651001.8532 | 5511241.2838
30390 | 651099.1658 | 5511231.3171
17087 | 650983.6115 | 5511211.9244
25791 | 651033.4693 | 5511356.0998
16582 | 651092.6905 | 5511232.1951
20680 | 651045.8586 | 5511352.9134
27337 | 650939.7203 | 5511243.6192
27338 | 650938.8679 | 5511228.2721
23763 | 650970.997 | 5511241.1554
23764 | 650976.0472 | 5511167.4971
13014 | 650803.1912 | 5511242.6708
23256 | 650728.7304 | 5511259.4775
19705 | 650669.8577 | 5511255.0981
17155 | 651080.3375 | 5511212.7443
21767 | 651058.5608 | 5511257.7062
13076 | 651112.0759 | 5511269.7222
30999 | 651083.7111 | 5511178.5884
26400 | 650969.6336 | 5511241.2819
26401 | 650969.9035 | 5511235.2576
20267 | 651064.6895 | 5511163.1777
22836 | 650980.6355 | 5511238.7055
18229 | 650667.4508 | 5511253.0393
22837 | 650981.0932 | 5511250.1757
23873 | 650874.2593 | 5511250.3849
17221 | 650872.4339 | 5511236.0013
25929 | 650972.2539 | 5511241.0388
25422 | 651102.0634 | 5511259.6872
27474 | 651081.9973 | 5511178.6599
30059 | 650757.2426 | 5511259.7987
17261 | 651099.9311 | 5511274.7553
29550 | 651033.7358 | 5511322.1619
13174 | 651023.6122 | 5511233.5706
33146 | 650873.3511 | 5511251.4689
24978 | 651034.7739 | 5511291.491
14739 | 651000.4867 | 5511257.9094
24979 | 651028.3048 | 5511291.7462
26522 | 651055.729 | 5511252.2624
24987 | 650653.6074 | 5511231.7213
24988 | 650656.7669 | 5511206.0013
28578 | 650850.3108 | 5511253.4495
23463 | 650901.4171 | 5511247.9946
25512 | 651111.474 | 5511260.3317
24489 | 651050.5887 | 5511266.9398
19889 | 650653.8471 | 5511203.6242
21943 | 650671.3047 | 5511253.9906
30136 | 651098.2705 | 5511210.6511
14786 | 651082.2877 | 5511173.4604
14787 | 651053.2677 | 5511283.1218
20423 | 651102.0768 | 5511293.641
17868 | 650601.9688 | 5511192.2785
18894 | 650850.7147 | 5511256.3722
32722 | 650670.7106 | 5511253.6958
24051 | 650922.0127 | 5511231.4773
24052 | 650924.7089 | 5511245.2557
28155 | 651098.0091 | 5511202.9083

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | endtemp_degree | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYM 4x1.5 | 0 | 12.1187 | 0.10776 | 0.025 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.43103 | 0
NYCWY 3x70/35 | 1120 | 0.26995 | 0.07477 | 0.227 | cs | 0 | 0.00393 | 160 | 1.0798 | 0.29908 | 672
NAYCWY 3x50/50 | 980 | 0.6417 | 0.077597 | 0.142 | cs | 0 | 0.00403 | 160 | 2.5668 | 0.31039 | 588
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
NAYBY 4x70sm 0.6/1kV | 810 | 0.4442 | 0.075398 | 0.175 | cs | 70 | 0.00403 | 160 | 1.7767 | 0.30159 | 367.6
NAYY 4x95SE 0.6/1kV | 770 | 0.3208 | 0.081996 | 0.211 | cs | 95 | 0.00403 | 160 | 1.2833 | 0.32798 | 349.2
NAYCWY 3x35/16 | 960 | 0.86558 | 0.078854 | 0.123 | cs | 0 | 0.00403 | 160 | 3.4623 | 0.31542 | 576
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NYCWY 3x25/25 | 840 | 0.72796 | 0.080739 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9118 | 0.32296 | 504
NYY-J 3x240SM 0.6/1kV | 1390 | 0.0777 | 0.072571 | 0.56 | cs | 240 | 0.00393 | 160 | 0.3106 | 0.29028 | 643.2
NKBA 4x95sm 0.6/1kV | 1000 | 0.1953 | 0.065973 | 0.28 | cs | 95 | 0.00393 | 180 | 0.7812 | 0.26389 | 514.6
NAYY 4x185SE 0.6/1kV | 830 | 0.165 | 0.080425 | 0.307 | cs | 185 | 0.00403 | 160 | 0.66 | 0.3217 | 385.9
NYY 4x10 | 0 | 1.8303 | 0.094562 | 0.075 | cs | 0 | 0.00393 | 160 | 7.3214 | 0.37825 | 0
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A_air | 12.6 | 0.413 | 0.29 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYY-J 4x16 | 0 | 1.1534 | 0.089535 | 0.098 | cs | 0 | 0.00393 | 160 | 4.6135 | 0.35814 | 0
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
NA2XS(F)2Y 1x150RM 12/20kV ir | 254 | 0.227 | 0.19541 | 0.353 | cs | 150 | 0.00403 | 250 | 0.832 | 0.309 | 253.6
NYY-O 3x120SM 0.6/1kV | 1309.9999 | 0.154 | 0.073199 | 0.309 | cs | 120 | 0.00393 | 160 | 0.6159 | 0.2928 | 569.7
NAYBY 4x150sm 0.6/1kV | 910 | 0.2075 | 0.072257 | 0.27 | cs | 150 | 0.00403 | 160 | 0.83 | 0.28903 | 441.1
NYY-J 4x25 | 0 | 0.72712 | 0.087965 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9085 | 0.35186 | 0
NYCWY 3x16/16 | 800 | 1.1534 | 0.08231 | 0.099 | cs | 0 | 0.00393 | 160 | 4.6135 | 0.32924 | 480
NYCWY 3x35/35 | 960 | 0.52486 | 0.077912 | 0.156 | cs | 0 | 0.00393 | 160 | 2.0995 | 0.31165 | 576
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NAYY 4x70SE 0.6/1kV | 750 | 0.4442 | 0.08231 | 0.176 | cs | 70 | 0.00403 | 160 | 1.7767 | 0.32924 | 312.4
NYY-O 3x70SM 0.6/1kV | 1130 | 0.2686 | 0.07477 | 0.225 | cs | 70 | 0.00393 | 160 | 1.0745 | 0.29908 | 477.8
NA2XS(F)2Y 1x240RM 12/20kV ir | 304 | 0.144 | 0.18253 | 0.456 | cs | 240 | 0.00403 | 250 | 0.749 | 0.303 | 303.2
NA2XS2Y 1x240RM 12/20kV ir | 304 | 0.144 | 0.18253 | 0.456 | cs | 240 | 0.00403 | 250 | 0.749 | 0.303 | 303.2
NEKBA 3x70rm 12/20kV | 280 | 0.2705 | 0.11624 | 0.22 | cs | 70 | 0.00393 | 155 | 1.0821 | 0.46496 | 284.9
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
15-AL1/3-ST1A 0.4_air | 11 | 1.8769 | 0.35 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
NAEKBA 3x95rm 12/20kV | 310 | 0.3203 | 0.10996 | 0.21 | cs | 95 | 0.00403 | 155 | 1.2814 | 0.43982 | 314.3
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
NYCWY 3x95/95 | 1160 | 0.19473 | 0.07477 | 0.272 | cs | 0 | 0.00393 | 160 | 0.77894 | 0.29908 | 696
NYY-J 3x70SM 0.6/1kV | 1130 | 0.2686 | 0.07477 | 0.276 | cs | 70 | 0.00393 | 160 | 1.0745 | 0.29908 | 477.8
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
N2XS(F)2Y 1x300RM/25 12/20kV it | 329 | 0.065 | 0.10996 | 0.597 | cs | 300 | 0.00393 | 250 | 0.2599 | 0.43982 | 328
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
NA2XS(F)2Y 1x95RM 12/20kV ir | 216 | 0.334 | 0.20986 | 0.282 | cs | 95 | 0.00403 | 250 | 1.134 | 0.563 | 215
NA2XS2Y 1x120RM 12/20kV ir | 235 | 0.267 | 0.20326 | 0.32 | cs | 120 | 0.00403 | 250 | 1.065 | 0.56 | 234.3
48-AL1/8-ST1A 0.4_air | 12.2 | 0.5939 | 0.3 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NAEKBA 3x120rm 12/20kV | 350 | 0.2534 | 0.10681 | 0.235 | cs | 120 | 0.00403 | 155 | 1.0136 | 0.42726 | 346.4
NA2YSY 1x150rm 12/20kV ir | 260 | 0.2092 | 0.11624 | 0.325 | cs | 150 | 0.00403 | 150 | 0.8367 | 0.46496 | 275.7
NKBA 4x70sm 0.6/1kV | 880 | 0.2707 | 0.069115 | 0.235 | cs | 70 | 0.00393 | 180 | 1.0827 | 0.27646 | 441.1
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
NKBA 4x120sm 0.6/1kV | 1140 | 0.1556 | 0.065973 | 0.32 | cs | 120 | 0.00393 | 180 | 0.6224 | 0.26389 | 606.5
NYY-J 4x35 | 0 | 0.52403 | 0.085137 | 0.156 | cs | 0 | 0.00393 | 160 | 2.0961 | 0.34055 | 0
NYM 4x50 | 0 | 0.38696 | 0.084823 | 0.185 | cs | 0 | 0.00393 | 160 | 1.5478 | 0.33929 | 0
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NYY-J 3x95SM 0.6/1kV | 1160 | 0.1941 | 0.07477 | 0.332 | cs | 95 | 0.00393 | 160 | 0.7766 | 0.29908 | 496.2
NYCY 4x16/16 | 800 | 1.15 | 0.089535 | 0.102 | cs | 0 | 0.00393 | 160 | 4.6 | 0.35814 | 480
NAYY-J 4x35 | 0 | 0.869 | 0.085137 | 0.123 | cs | 0 | 0 | 160 | 3.476 | 0.34055 | 0
NA2YSY 1x95rm 12/20kV ir | 230 | 0.3225 | 0.12566 | 0.265 | cs | 95 | 0.00403 | 150 | 1.29 | 0.50265 | 238.9
NYY-J 4x50 | 0 | 0.38696 | 0.084823 | 0.185 | cs | 0 | 0.00393 | 160 | 1.5478 | 0.33929 | 0
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
NAYBY 4x50sm 0.6/1kV | 710 | 0.6417 | 0.07854 | 0.14 | cs | 50 | 0.00403 | 160 | 2.5667 | 0.31416 | 312.4
NYY-O 3x240SM 0.6/1kV | 1390 | 0.0777 | 0.072571 | 0.458 | cs | 240 | 0.00393 | 160 | 0.3106 | 0.29028 | 643.2
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
NYY-O 3x150SM 0.6/1kV | 1320.0001 | 0.1255 | 0.073199 | 0.348 | cs | 150 | 0.00393 | 160 | 0.5021 | 0.2928 | 588.1
N2XS(F)2Y 1x400RM/35 12/20kV it | 368 | 0.0535 | 0.11153 | 0.671 | cs | 400 | 0.00393 | 250 | 0.214 | 0.44611 | 366.6
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
94-AL1/15-ST1A 0.4_air | 13.2 | 0.306 | 0.29 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYY-J 3x150SM 0.6/1kV | 1320.0001 | 0.1255 | 0.073199 | 0.426 | cs | 150 | 0.00393 | 160 | 0.5021 | 0.2928 | 588.1
NAYCWY 3x120/120 | 1280 | 0.3221 | 0.073199 | 0.24 | cs | 0 | 0.00403 | 160 | 1.2884 | 0.2928 | 768
NYCWY 3x50/50 | 980 | 0.3878 | 0.077597 | 0.184 | cs | 0 | 0.00393 | 160 | 1.5512 | 0.31039 | 588
NAYY-J 3x35/35 | 0 | 0.869 | 0.085137 | 0.123 | cs | 0 | 0 | 160 | 3.476 | 0.34055 | 0
NYCWY 3x95/50 | 1160 | 0.19473 | 0.07477 | 0.272 | cs | 0 | 0.00393 | 160 | 0.77894 | 0.29908 | 696
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
24-AL1/4-ST1A 0.4_air | 11.25 | 1.2012 | 0.335 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
NAYY 4x150SE 0.6/1kV | 830 | 0.2067 | 0.080425 | 0.27 | cs | 150 | 0.00403 | 160 | 0.8267 | 0.3217 | 385.9
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NAYY 4x120SE 0.6/1kV | 840 | 0.2542 | 0.080425 | 0.24 | cs | 120 | 0.00403 | 160 | 1.0167 | 0.3217 | 385.9
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
NAEKBA 3x50rm 12/20kV | 240 | 0.6415 | 0.12252 | 0.14 | cs | 50 | 0.00403 | 155 | 2.5661 | 0.49009 | 248.1
NEKBA 3x50rm 12/20kV | 240 | 0.3913 | 0.12252 | 0.18 | cs | 50 | 0.00393 | 155 | 1.5653 | 0.49009 | 248.1
N2YSY 1x70rm 12/20kV ir | 200 | 0.2711 | 0.13195 | 0.285 | cs | 70 | 0.00393 | 150 | 1.0845 | 0.52779 | 211.3
MS-Leitungstyp_fiktiv | 0 | 0 | 0 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NAYY-J 4x50 | 0 | 0.641 | 0.084823 | 0.144 | cs | 0 | 0 | 160 | 2.564 | 0.33929 | 0
NA2YSY 1x240rm 12/20kV ir | 310 | 0.1292 | 0.10996 | 0.425 | cs | 240 | 0.00403 | 150 | 0.5167 | 0.43982 | 321.6
NAYY 4x240SE 0.6/1kV | 870 | 0.1267 | 0.079796 | 0.357 | cs | 240 | 0.00403 | 160 | 0.5067 | 0.31919 | 422.7
NYCWY 3x25/16 | 840 | 0.72796 | 0.080739 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9118 | 0.32296 | 504
NEKBA 3x95rm 12/20kV | 310 | 0.1948 | 0.10996 | 0.27 | cs | 95 | 0.00393 | 155 | 0.7792 | 0.43982 | 314.3
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
NAEKBA 3x150rm 12/20kV | 370 | 0.2076 | 0.10367 | 0.265 | cs | 150 | 0.00403 | 155 | 0.8305 | 0.41469 | 374
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 1x240RM 0.6/1kV ir | 800 | 0.1258 | 0.17719 | 0.432 | cs | 240 | 0.00403 | 160 | 0.5033 | 0.70874 | 808.6
MS/FL-Al/St 95/15 (410107)_air | 10 | 0.304 | 0.373 | 1 | ol | 0 | 0.00403 | 80 | 0.452 | 1.464 | 4
NAYBY 4x95sm 0.6/1kV | 840 | 0.3208 | 0.075398 | 0.21 | cs | 95 | 0.00403 | 160 | 1.2833 | 0.30159 | 404.3
NKBA 0.6/1 kV 3x50/ 25sm | 680 | 0.387 | 0.087996 | 0.191 | cs | 50 | 0.00393 | 180 | 1.548 | 0.35198 | 408
NYY 4x6 | 0 | 3.084 | 0.10085 | 0.056 | cs | 0 | 0.00393 | 160 | 12.336 | 0.40338 | 0
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
NYY-J 4x120 | 0 | 0.15378 | 0.080425 | 0.313 | cs | 0 | 0.00393 | 160 | 0.61513 | 0.3217 | 0
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NKBA 0.6/1 kV 3x35/ 16sm | 590 | 0.524 | 0.090981 | 0.161 | cs | 35 | 0.00393 | 180 | 2.096 | 0.36392 | 354
NYY 4x1.5 | 0 | 12.1187 | 0.11498 | 0.026 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.45993 | 0
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
NKBA 4x50sm 0.6/1kV | 760 | 0.3914 | 0.069115 | 0.19 | cs | 50 | 0.00393 | 180 | 1.5656 | 0.27646 | 349.2
NS-Leitungstyp_fiktiv | 0 | 0 | 0 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
NYCWY 3x70/70 | 1120 | 0.26995 | 0.07477 | 0.227 | cs | 0 | 0.00393 | 160 | 1.0798 | 0.29908 | 672
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NYY-J 3x185SM 0.6/1kV | 1320.0001 | 0.1013 | 0.073199 | 0.483 | cs | 185 | 0.00393 | 160 | 0.405 | 0.2928 | 588.1
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
NAYCWY 3x35/35 | 960 | 0.86558 | 0.078854 | 0.123 | cs | 0 | 0.00403 | 160 | 3.4623 | 0.31542 | 576
NYY 4x2.5 | 0 | 7.4133 | 0.10681 | 0.034 | cs | 0 | 0.00393 | 160 | 29.6532 | 0.42726 | 0
NYCWY 4x35/16 | 960 | 0.52486 | 0.085137 | 0.157 | cs | 0 | 0.00393 | 160 | 2.0995 | 0.34055 | 576
NKBA 4x35sm 0.6/1kV | 590 | 0.524 | 0.091012 | 0.161 | cs | 35 | 0.00393 | 180 | 2.096 | 0.36405 | 590
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
NYY 4x4 | 0 | 4.6135 | 0.1065 | 0.044 | cs | 0 | 0.00393 | 160 | 18.4538 | 0.426 | 0
NA2XY 3x150sm 0.6/1kV | 610 | 0.207 | 0.069115 | 0.3 | cs | 150 | 0.00403 | 250 | 0.8281 | 0.27646 | 238.9
NYY 3x1.5 | 0 | 12.1187 | 0.10776 | 0.025 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.43103 | 0

## trafo_std_types
| sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | vector_group | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
MSNS_0126 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0062 | 0.4 | 20 | 0.4 | 4.16 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0008 | 0.63 | 20 | 0.4 | 4.04 | 0.7627 | 0.556 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0138 | 0.63 | 20 | 0.4 | 4 | 0.83937 | 0.542 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0150 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0141 | 0.63 | 20 | 0.4 | 4.1 | 0.83063 | 0.819 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0089 | 0.4 | 20 | 0.4 | 3.74 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0060 | 0.4 | 20 | 0.4 | 3.825 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0091 | 0.4 | 20 | 0.4 | 3.87 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0087 | 0.4 | 20 | 0.4 | 3.98 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0163 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0059 | 0.8 | 20 | 0.4 | 4.2 | 0.875 | 0.8 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0080 | 0.63 | 20 | 0.4 | 4.1 | 0.85937 | 0.589 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0153 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0148 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0140 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0061 | 0.63 | 20 | 0.4 | 3.9 | 0.71 | 0.562 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0077 | 0.315 | 20 | 0.4 | 3.89 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0039 | 0.4 | 20 | 0.4 | 3.8 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0161 | 0.63 | 20 | 0.4 | 4.25 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0017 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0011 | 0.4 | 20 | 0.4 | 4.14 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0040 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0121 | 0.515 | 20 | 0.4 | 4.1 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0051 | 0.63 | 20 | 0.4 | 4.11 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
160 MVA 380/110 kV | 160 | 380 | 110 | 12.2 | 0.25 | 60 | 0.06 | 0 | Yy0 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
MSNS_0137 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0004 | 0.4 | 20 | 0.4 | 4.01 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0093 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0147 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0013 | 0.515 | 20 | 0.4 | 4 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0172 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0046 | 0.4 | 20 | 0.4 | 3.85 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0021 | 0.4 | 20 | 0.4 | 3.8 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0124 | 0.63 | 20 | 0.4 | 3.7 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0102 | 0.315 | 20 | 0.4 | 3.95 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0018 | 0.4 | 20 | 0.4 | 4.25 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0107 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0164 | 0.4 | 20 | 0.4 | 3.81 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0005 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0135 | 0.63 | 20 | 0.4 | 3.94 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0035 | 0.63 | 20 | 0.4 | 4 | 0.84317 | 0.566 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0181 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0073 | 0.4 | 20 | 0.4 | 3.9 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0123 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0067 | 0.4 | 20 | 0.4 | 4.13 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0167 | 0.63 | 20 | 0.4 | 4.04 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0081 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.25 MVA 10/0.4 kV | 0.25 | 10 | 0.4 | 4 | 1.2 | 0.6 | 0.24 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
MSNS_0086 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0195 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0149 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0128 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0146 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0047 | 0.63 | 20 | 0.4 | 4.3 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0106 | 0.63 | 20 | 0.4 | 3.95 | 0.78238 | 0.5945 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0015 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0198 | 0.515 | 20 | 0.4 | 3.9 | 1.0485 | 0.30191 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.25 MVA 20/0.4 kV | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | Yzn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
MSNS_0025 | 0.4 | 20 | 0.4 | 3.81 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0029 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0160 | 0.315 | 20 | 0.4 | 4 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
40 MVA 110/10 kV | 40 | 110 | 10 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
MSNS_0054 | 0.2 | 20 | 0.4 | 4.22 | 1 | 0.2 | 0.3 | 150 | Yz5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0129 | 0.63 | 20 | 0.4 | 4.2 | 0.83238 | 0.581 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.63 MVA 20/0.4 kV | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
MSNS_0076 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0068 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.4 MVA 20/0.4 kV | 0.4 | 20 | 0.4 | 6 | 1.425 | 1.35 | 0.3375 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
MSNS_0194 | 0.63 | 20 | 0.4 | 4.2 | 0.81079 | 0.546 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0042 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0053 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0056 | 0.2 | 20 | 0.4 | 3.86 | 1 | 0.2 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0078 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0098 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0069 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0101 | 0.63 | 20 | 0.4 | 4 | 0.71127 | 0.588 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0085 | 0.4 | 20 | 0.4 | 3.87 | 0.7625 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_1000 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0057 | 0.4 | 20 | 0.4 | 4.88 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.4 MVA 10/0.4 kV | 0.4 | 10 | 0.4 | 4 | 1.325 | 0.95 | 0.2375 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
MSNS_0063 | 0.4 | 20 | 0.4 | 3.81 | 0.9605 | 0.397 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
OR 40000/110 27332688 | 40 | 115.1 | 21 | 13.92 | 0.38255 | 19.613 | 0.05 | 150 | YNd5 | 0 | 0 | 100 | 0 | 0.9
63 MVA 110/20 kV | 63 | 110 | 20 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
MSNS_0156 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0009 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0142 | 0.2 | 20 | 0.4 | 4 | 1.15 | 0.22 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0044 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0028 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0131 | 0.63 | 20 | 0.4 | 3.9 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0012 | 0.63 | 20 | 0.4 | 6 | 0.0011111 | 0.00099 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0108 | 0.4 | 20 | 0.4 | 4.2 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0092 | 0.4 | 20 | 0.4 | 3.54 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0050 | 0.4 | 20 | 0.4 | 4.2 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0158 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
25 MVA 110/10 kV | 25 | 110 | 10 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
MSNS_0185 | 0.63 | 20 | 0.4 | 3.89 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0058 | 0.515 | 20 | 0.4 | 4.025 | 0.87039 | 0.475 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0041 | 0.4 | 20 | 0.4 | 4.5 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0003 | 0.715 | 20 | 0.4 | 4.1 | 0.86713 | 0.7 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0162 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0034 | 0.63 | 20 | 0.4 | 3.82 | 0.00063492 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0192 | 0.63 | 20 | 0.4 | 4.16 | 0.76651 | 0.552 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0043 | 0.4 | 20 | 0.4 | 4.27 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0191 | 0.63 | 20 | 0.4 | 3.98 | 0.45984 | 0.523 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.63 MVA 10/0.4 kV | 0.63 | 10 | 0.4 | 4 | 1.0794 | 1.18 | 0.1873 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
MSNS_0113 | 0.4 | 20 | 0.4 | 4.1 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0133 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0196 | 0.4 | 20 | 0.4 | 3.79 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0109 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0097 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0104 | 0.4 | 20 | 0.4 | 4.05 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0014 | 0.4 | 20 | 0.4 | 3.9 | 0.6575 | 0.407 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0145 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0136 | 0.63 | 20 | 0.4 | 4.1 | 0.84317 | 0.844 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0175 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0036 | 0.4 | 20 | 0.4 | 3.75 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0001 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0020 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0052 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0019 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0079 | 0.4 | 20 | 0.4 | 3.8 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0168 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0169 | 0.25 | 20 | 0.4 | 3.8 | 0.35 | 0.09 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
25 MVA 110/20 kV | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
MSNS_0165 | 0.63 | 20 | 0.4 | 4.03 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0032 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0072 | 0.4 | 20 | 0.4 | 3.65 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0030 | 0.8 | 20 | 0.4 | 4.2 | 0.875 | 0.8 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0199 | 0.63 | 20 | 0.4 | 4.065 | 0.97048 | 0.784 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0177 | 0.63 | 20 | 0.4 | 3.77 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0120 | 0.4 | 20 | 0.4 | 4.45 | 1.2 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0016 | 0.4 | 20 | 0.4 | 3.48 | 1.05 | 0.43 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0088 | 0.515 | 20 | 0.4 | 4 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0045 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0048 | 0.4 | 20 | 0.4 | 3.79 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0037 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
40 MVA 110/20 kV | 40 | 110 | 20 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 63 | 110 | 10 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
MSNS_0103 | 0.4 | 20 | 0.4 | 3.65 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0112 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0186 | 0.63 | 20 | 0.4 | 3.9 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0074 | 0.4 | 20 | 0.4 | 4.1 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0170 | 0.63 | 20 | 0.4 | 4.12 | 0.77762 | 0.567 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
100 MVA 220/110 kV | 100 | 220 | 110 | 12 | 0.26 | 55 | 0.06 | 0 | Yy0 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | description | object
6 | bus | substat | object
7 | bus | folder_id | object
8 | bus | sernum | object
9 | bus | for_name | object
10 | bus | chr_name | object
11 | load | name | object
12 | load | bus | uint32
13 | load | p_mw | float64
14 | load | q_mvar | float64
15 | load | const_z_percent | float64
16 | load | const_i_percent | float64
17 | load | sn_mva | float64
18 | load | scaling | float64
19 | load | in_service | bool
20 | load | type | object
21 | load | description | object
22 | load | sernum | object
23 | load | for_name | object
24 | load | chr_name | object
25 | sgen | name | object
26 | sgen | bus | int64
27 | sgen | p_mw | float64
28 | sgen | q_mvar | float64
29 | sgen | sn_mva | float64
30 | sgen | scaling | float64
31 | sgen | in_service | bool
32 | sgen | type | object
33 | sgen | current_source | bool
34 | sgen | description | object
35 | sgen | sernum | object
36 | sgen | for_name | object
37 | sgen | chr_name | object
38 | switch | bus | int64
39 | switch | element | int64
40 | switch | et | object
41 | switch | type | object
42 | switch | closed | bool
43 | switch | name | object
44 | switch | z_ohm | float64
45 | ext_grid | name | object
46 | ext_grid | bus | uint32
47 | ext_grid | vm_pu | float64
48 | ext_grid | va_degree | float64
49 | ext_grid | slack_weight | float64
50 | ext_grid | in_service | bool
51 | ext_grid | s_sc_max_mva | float64
52 | ext_grid | s_sc_min_mva | float64
53 | ext_grid | rx_min | float64
54 | ext_grid | rx_max | float64
55 | ext_grid | r0x0_max | float64
56 | ext_grid | x0x_max | float64
57 | ext_grid | r0x0_min | float64
58 | ext_grid | x0x_min | float64
59 | ext_grid | description | object
60 | line | name | object
61 | line | std_type | object
62 | line | from_bus | uint32
63 | line | to_bus | uint32
64 | line | length_km | float64
65 | line | r_ohm_per_km | float64
66 | line | x_ohm_per_km | float64
67 | line | c_nf_per_km | float64
68 | line | g_us_per_km | float64
69 | line | max_i_ka | float64
70 | line | df | float64
71 | line | parallel | uint32
72 | line | type | object
73 | line | in_service | bool
74 | line | r0_ohm_per_km | float64
75 | line | x0_ohm_per_km | float64
76 | line | c0_nf_per_km | float64
77 | line | alpha | float64
78 | line | temperature_degree_celsius | float64
79 | line | description | object
80 | line | line_idx | float64
81 | line | folder_id | object
82 | line | section_idx | int64
83 | trafo | name | object
84 | trafo | std_type | object
85 | trafo | hv_bus | uint32
86 | trafo | lv_bus | uint32
87 | trafo | sn_mva | float64
88 | trafo | vn_hv_kv | float64
89 | trafo | vn_lv_kv | float64
90 | trafo | vk_percent | float64
91 | trafo | vkr_percent | float64
92 | trafo | pfe_kw | float64
93 | trafo | i0_percent | float64
94 | trafo | shift_degree | float64
95 | trafo | tap_side | object
96 | trafo | tap_neutral | float64
97 | trafo | tap_min | float64
98 | trafo | tap_max | float64
99 | trafo | tap_step_percent | float64
100 | trafo | tap_step_degree | float64
101 | trafo | tap_pos | int32
102 | trafo | tap_phase_shifter | bool
103 | trafo | parallel | uint32
104 | trafo | df | float64
105 | trafo | in_service | bool
106 | trafo | vk0_percent | float64
107 | trafo | vkr0_percent | float64
108 | trafo | mag0_percent | float64
109 | trafo | mag0_rx | float64
110 | trafo | si0_hv_partial | float64
111 | trafo | tap_set_vm_pu | float64
112 | trafo | description | object
113 | trafo | equipment | object
114 | line_geodata | coords | object
115 | bus_geodata | x | float64
116 | bus_geodata | y | float64
117 | bus_geodata | coords | object