## bus
| name | vn_kv | type | zone | in_service | description | substat | folder_id | sernum | for_name | chr_name
15873 | 7068068_001001_005005_00340034_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | FDE9D57694974E8FAB57689EAEB76E7E
20997 | 7068068_001001_005005_00400040_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 52E857166DD94ED39A9CA13701AA81BB
29701 | 7068068_001001_005005_01060106_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
33286 | 7068068_001001_005005_00640064_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
28680 | 7068068_001001_005005_01120112_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
15884 | 7068068_001001_005005_00360036_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | DF12EC2F771E43EF89DC6FF3D2F3A307
15888 | 7068068_001001_005005_00420042_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 96B40AF86EFE4218963903116C580EB2
24593 | 7068068_001001_005005_00230023_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19994 | 7068068_001001_005005_00280028_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 585F1DEBBA5D46698019D9F165DB0348
27169 | 7068068_001001_004004_00040004_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
31269 | 7068068_001001_005005_00630063_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
29734 | 7068068_001001_003003_00170017_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
16423 | 7068068_001001_005005_00930093_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 47089EB2D4D24AE1A3D03C707547B314
20008 | 7068068_001001_005005_00130013_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | C0B2569EEA744844A9DFC662873A5887
20521 | 7068068_001001_005005_00550055_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 589EB8C4FA66431E89FAA989E4B2688E
28205 | 7068068_001001_005005_00940094_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
23093 | 7068068_001001_001001_00010002_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
29239 | 7068068_001001_005005_00880088_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
13368 | 7068068_001001_005005_00850085_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 9BB31C433E404AF3B005869F09A2534E
18493 | 7068068_001001_004004_00030003_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 0D8DB958CE79481B87756731CCA0E710
27709 | 7068068_001001_005005_00490050_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
33342 | 7068068_001001_005005_00010002_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
19522 | 7068068_001001_004004_00090009_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | FDB4D7F80BBA4A18B55242E0C9A97803
28230 | 7068068_001001_004004_00260026_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
25671 | 7068068_001001_005005_00900090_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
31305 | 7068068_001001_005005_01100110_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
21071 | 7068068_001001_005005_00440044_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 55A724F60E5842CDB3E010F818039971
15953 | 7068068_001001_005005_00790079_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | FEE578783642476DB380CB367ED0A599
20561 | 7068068_001001_005005_01070107_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 4AD77C26DF1E48E290226A64305F2904
24658 | 7068068_001001_003003_00060006_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
27738 | 7068068_001001_005005_00310031_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
22621 | 7068068_001001_005005_00040005_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
19040 | 7068068_001001_004004_00290029_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 16FED0AD509544AC8EF492B51B76D92F
23140 | 7068068_001001_005005_00380038_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
31845 | 7068068_001001_005005_00180020_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
20074 | 7068068_001001_002002_00020002_01003 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 0A78D6D6981B4B92A50EF09D86CD9E8C
33388 | 7068068_001001_005005_00620062_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
24173 | 7068068_001001_004004_00180018_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
14447 | 7068068_001001_005005_01030103_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | CC57B671D7104CB1BBE249CD119C898E
27767 | 7068068_001001_005005_01000100_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
18552 | 7068068_001001_005005_00030003_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | D402E6FAB9644E5382624AADB6CC2052
24696 | 7068068_001001_004004_00140014_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
23675 | 7068068_001001_005005_01080108_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
31372 | 7068068_001001_005005_00080008_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
27793 | 7068068_001001_005005_00840084_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
17042 | 7068068_001001_005005_00570057_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 98BB346B9AF74476993F020618237748
29332 | 7068068_001001_005005_00180018_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19100 | 7068068_001001_003003_00090009_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 19256A29708541C7A53BF999A3C7ECB3
19101 | 7068068_001001_005005_00070007_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | F60BE66D6DFB43F8B4E3550A5417781B
26780 | 7068068_001001_005005_00760076_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
28832 | 7068068_001001_005005_00720072_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
24742 | 7068068_001001_005005_00160017_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
24743 | 7068068_001001_005005_00160016_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
20136 | 7068068_001001_004004_00230023_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 24A137E1DFE14F239259327D6008E5AA
21166 | 7068068_001001_005005_00110011_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | B1A3FD86F4064D1DB8FF2D4D9658A3AA
28850 | 7068068_001001_005005_00120012_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
28851 | 7068068_001001_005005_00330034_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
24246 | 7068068_001001_002002_00010002_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
24247 | 7068068_001001_002002_00010002_01002 | 0.4 | m | SWF | TRUE |  |  | SWF
21688 | 7068068_001001_003003_00040004_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
16058 | 7068068_001001_004004_00270027_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 393F68F2F59C4ED2984A156F6AD46EED
31418 | 7068068_001001_003003_00100010_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
23229 | 7068068_001001_005005_00140015_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
13509 | 7068068_001001_003003_00070007_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 89483F077832487BA71145C99A900644
19147 | 7068068_001001_005005_00090009_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | E94C9C3219AC4651B14B18D76121BE58
28365 | 7068068_001001_005005_00740074_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
31950 | 7068068_001001_005005_00250025_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
31952 | 7068068_001001_003003_00010002_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
31953 | 7068068_001001_003003_00010002_01002 | 0.4 | m | SWF | TRUE |  |  | SWF
24786 | 7068068_001001_005005_01020102_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19156 | 7068068_001001_005005_00050005_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | A59E943D36674258BA4746B45D63C7F6
23774 | 7068068_001001_005005_00180019_01002 | 0.4 | m | SWF | TRUE |  |  | SWF
15583 | 7068068_001001_004004_00170017_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | BFBC2C40793A405D820D02B299D13E4C
14561 | 7068068_001001_005005_00770077_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | EE6B428F2A48460B8967B2707229EC76
28898 | 7068068_001001_005005_00430044_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
17124 | 7068068_001001_005005_01110111_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 84146CEA82424654B2C2EA475581A040
16101 | 7068068_001001_005005_00480048_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 6A7E3AFD655B4B5DA7AA4C516AD46AB2
19686 | 7068068_001001_004004_00070007_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 484FA2AED82440D9941A2BDBFC82D334
23269 | 7068068_001001_005005_00960096_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
29414 | 7068068_001001_005005_00920092_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
17130 | 7068068_001001_005005_00240024_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | E7273FCA6B70473D94B00490B83BD30A
18160 | 7068068_001001_005005_00970097_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 55011EA5CBF04DDA802D345CD8215C05
33520 | 7068068_001001_005005_01160116_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
20723 | 7068068_001001_003003_00130013_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | BCB1F5329F744472994A7244258A04D7
25331 | 7068068_001001_004004_00280028_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
27379 | 7068068_001001_003003_00140014_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
15617 | 7068068_001001_005005_00870087_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 6CD331BDDF664F1DBCDDAA602F37D5E3
14594 | 7068068_001001_005005_01010101_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 688CB07DE7814AA9A219AA63148D32EF
21249 | 7068068_001001_004004_00250025_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | E7B5B19B3E0B466D8BA115CFCCD22CC2
16644 | 7068068_001001_003003_00030003_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 117BD8CE1B2242979574CB02FC9FE6EC
23810 | 7068068_001001_005005_00820082_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
27906 | 7068068_001001_005005_00080009_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
19210 | 7068068_001001_005005_00150015_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 1005E1F21571428C981FE1F99712A499
25867 | 7068068_001001_005005_01040104_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19216 | 7068068_001001_003003_00190019_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 7D867892447D47DAA6775A459F19AF7A
29465 | 7068068_001001_005005_00510052_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
21274 | 7068068_001001_005005_00950095_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 2E9667075BA24976B28A0D9AE603EB4D
29466 | 7068068_001001_005005_00510051_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
25886 | 7068068_001001_004004_00200020_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
18209 | 7068068_001001_005005_00590059_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 564165D86F9C4DC0B07886471D4BD694
20770 | 7068068_001001_005005_00890089_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 1F8E84F305794B33AA364347AD17ED0A
24866 | 7068068_001001_005005_00060007_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
29476 | 7068068_001001_005005_00430043_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
23333 | 7068068_001001_003003_00120012_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
14119 | 7068068_001001_003003_00160016_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | A5CD05AB91C549648169439CCC9B6132
21292 | 7068068_001001_005005_00710071_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | A3D40D17BF0E42F186A455C84DFC1075
14125 | 7068068_001001_005005_00670067_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 8BCEB11111524CED85D202A99CEB7E28
23853 | 7068068_001001_005005_00290029_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
29999 | 7068068_001001_004004_00020002_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19761 | 7068068_001001_005005_00810081_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | EB423AB282E14F48BCD3656A20966C3E
30513 | 7068068_001001_005005_00490049_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19255 | 7068068_001001_005005_00830083_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 352C754FF3BF40B1B1CBC906F3AD31C2
17208 | 7068068_001001_005005_00460046_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 80BA37ADC91541F891B5653AC734A551
19767 | 7068068_001001_005005_00610061_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | A0FC3311A4404A11A4669B02EAC3C28E
24384 | 7068068_001001_005005_00390042_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
14145 | 7068068_001001_004004_00110011_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 88F1CB381F264D5B9A10ACA68EDE5FC1
20289 | 7068068_001001_004004_00150015_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 58C0184DCDE2420AB3FB97062ACBFEBF
24385 | 7068068_001001_005005_00390039_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
33090 | 7068068_001001_005005_01140114_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
27461 | 7068068_001001_005005_00860086_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
13127 | 7068068_001001_005005_00170017_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 97D092224E604BDE951BAA41FACBA412
17736 | 7068068_001001_005005_00540054_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 43AEFF75C3164ED9B87C4DC43E5C4608
17231 | 7068068_001001_005005_01050105_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 7C52BA6E6BB34058997F92D35D16461F
19279 | 7068068_001001_003003_00050005_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | E84E2B5778854E72BC53BD9392D11676
19791 | 7068068_001001_005005_01090109_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 8A993D6447BE4FD0A377D08471E306DC
22864 | 7068068_001001_004004_00160016_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
31058 | 7068068_001001_004004_00100010_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
24919 | 7068068_001001_004004_00120012_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19288 | 7068068_001001_005005_00260026_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 6A57AC49D8ED483AA069F3E15134052A
16217 | 7068068_001001_005005_00300030_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | F5AC6DD82D374C9E9198845EDE2539F5
24409 | 7068068_001001_005005_00580058_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
30041 | 7068068_001001_005005_00530053_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
13662 | 7068068_001001_005005_00750075_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 76A8B7190D834B2E80B58979FEDA7C51
17759 | 7068068_001001_005005_00410041_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | EB8508E4BA9341659A2CB41853187537
13668 | 7068068_001001_003003_00150015_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | ACCC4A0E481544659AD4C5E674BEB283
29540 | 7068068_001001_004004_00220022_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
29541 | 7068068_001001_005005_00980098_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
28011 | 7068068_001001_005005_00270027_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
24940 | 7068068_001001_005005_01150115_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
29177 | 7068068_001001_003003_00020002_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
30063 | 7068068_001001_005005_00100010_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
13172 | 7068068_001001_005005_00910091_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 2E71316F42FD4A3EAAECD24C5919D41B
33142 | 7068068_001001_005005_00980100_01002 | 0.4 | m | SWF | TRUE |  |  | SWF
15737 | 7068068_001001_005005_00520052_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | ECB53282142F46FA8547E11375910AC6
24441 | 7068068_001001_005005_00210021_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
33148 | 7068068_001001_004004_00010002_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
16765 | 7068068_001001_005005_00990099_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | D86E5B4E3908413191EF3A64E015D9E3
23421 | 7068068_001001_004004_00240024_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
24958 | 7068068_001001_005005_00780078_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
33149 | 7068068_001001_004004_00300030_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
20868 | 7068068_001001_005005_00690069_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 1B0DB620BA584F26BC84DE4D7A79D0D9
24965 | 7068068_001001_005005_00040004_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
24966 | 7068068_001001_005005_00560056_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19849 | 7068068_001001_005005_00500050_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 14B53225A78F411BAD237F6A025F123A
28045 | 7068068_001001_005005_00530054_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
27031 | 7068068_001001_005005_00600060_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
32664 | 7068068_001001_005005_00370037_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
31130 | 7068068_001001_004004_00060006_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
15784 | 7068068_001001_005005_01170117_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 1728C944FA1145518DC52A30D5AF1A01
29618 | 7068068_001001_005005_00330033_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
22454 | 7024024_001001_005005_02500252_01183 | 21 | b | SWF | TRUE |  |  | SWF
22455 | 7068068_001001_000000_00010001_02001 | 0.4 | b | SWF | TRUE |  |  | SWF
27063 | 7068068_001001_004004_00080008_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
15293 | 7068068_001001_005005_00320032_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 0933A437086E4E00A61AFDFBD09D14D2
13757 | 7068068_001001_005005_00190019_01003 | 0.4 | m | SWF | TRUE |  |  | SWF |  | ECB687A76C6942E1805A8FFE934FB2B3
16829 | 7068068_001001_005005_01180118_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 3A1C031D90B64049B3845EECBC619B6C
31166 | 7068068_001001_005005_00680068_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
21443 | 7068068_001001_004004_00210021_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 4D473C4105BD45FCBD29550215D24844
20420 | 7068068_001001_005005_00650065_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | E5CDBB1A1A1641D4A00E1FF7794C20C8
33220 | 7068068_001001_005005_00980100_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
24006 | 7068068_001001_005005_00020002_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
24007 | 7068068_001001_005005_00020003_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
29641 | 7068068_001001_003003_00110011_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
21962 | 7068068_001001_005005_00200020_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
28114 | 7068068_001001_005005_00800080_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
25044 | 7068068_001001_005005_00350035_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
28628 | 7068068_001001_005005_00180019_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
19414 | 7068068_001001_005005_00730073_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | EB68F8B378914C49867532BE2A47591F
24023 | 7068068_001001_005005_00700070_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
13273 | 7068068_001001_004004_00050005_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | A013252BEC7D4AA18DB54596F904890E
27613 | 7068068_001001_005005_00470048_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
27614 | 7068068_001001_005005_00470047_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
19423 | 7068068_001001_001001_00020002_01002 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 805DDA5C8F7E4C95982A280E76463EFC
13798 | 7068068_001001_004004_00190019_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | D4B36B28C4DB41C2B0AA7091828F9ADF
28134 | 7068068_001001_005005_00060006_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
20968 | 7068068_001001_003003_00180018_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | D420DE83FCD143E2ACF8EBB61FE814C6
23529 | 7068068_001001_005005_00220026_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
23530 | 7068068_001001_005005_00220022_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
15855 | 7068068_001001_005005_01130113_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | E365DBCF402647A6B50C07FF2530AEFA
14321 | 7068068_001001_004004_00130013_01001 | 0.4 | m | SWF | TRUE |  |  | SWF |  | 00448E2D32F64A37919125ADA6725E38
23025 | 7068068_001001_005005_00660066_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
23026 | 7068068_001001_005005_00450046_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
23027 | 7068068_001001_005005_00450045_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
25587 | 7068068_001001_005005_00120013_01001 | 0.4 | m | SWF | TRUE |  |  | SWF
23545 | 7068068_001001_003003_00080008_03001 | 0.4 | m | SWF | TRUE |  |  | SWF
27134 | 7068068_001001_005005_00140014_03001 | 0.4 | m | SWF | TRUE |  |  | SWF

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type | description | sernum | for_name | chr_name
189 |  | 21274 | 281.3855 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:281.386,file:000019889.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
190 |  | 21274 | 0.8174 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:189,demand:0.8174,file_add:000019890.csv,file:NaN,load_type:heat,temperature:55
191 |  | 21274 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:189,demand:0.011,file:NaN,file_add:000019891.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
192 |  | 21274 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:189,demand:0.011,file:NaN,file_add:000019892.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
193 |  | 21274 | 0.0115 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:189,demand:0.0115,file_add:000019893.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0115
171 |  | 21249 | 140.6927 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:140.693,file:000019863.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
95 |  | 21166 | 339.4327 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:339.433,file:000019764.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
156 |  | 20723 | 99.6075 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:99.608,file:000019844.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
157 |  | 20723 | 1.0823 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:156,demand:1.0822799999999997,file_add:000019845.csv,file:NaN,load_type:heat,temperature:55
158 |  | 20723 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:156,demand:0.011,file:NaN,file_add:000019846.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
159 |  | 20723 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:156,demand:0.011,file:NaN,file_add:000019847.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
160 |  | 20723 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:156,demand:0.011,file:NaN,file_add:000019848.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
161 |  | 20723 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:156,demand:0.011,file:NaN,file_add:000019849.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
162 |  | 20723 | 0.0187 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:156,demand:0.0187,file_add:000019850.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0187
60 |  | 20561 | 29.8295 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:29.83,file:000019718.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
245 |  | 20289 | 147.2205 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:147.22,file:000019963.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
246 |  | 20289 | 0.72032 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:245,demand:0.72032,file_add:000019964.csv,file:NaN,load_type:heat,temperature:55
247 |  | 20289 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:245,demand:0.011,file:NaN,file_add:000019965.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
248 |  | 20289 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:245,demand:0.011,file:NaN,file_add:000019966.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
249 |  | 20289 | 0.0059 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:245,demand:0.0059,file_add:000019967.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0059
89 |  | 20136 | 18.3987 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:18.399,file:000019755.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
90 |  | 20136 | 1.052 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:89,demand:1.052,file_add:000019756.csv,file:NaN,load_type:heat,temperature:55
91 |  | 20136 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:89,demand:0.011,file:NaN,file_add:000019757.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
92 |  | 20136 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:89,demand:0.011,file:NaN,file_add:000019758.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
93 |  | 20136 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:89,demand:0.011,file:NaN,file_add:000019759.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
94 |  | 20136 | 0.0203 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:89,demand:0.0203,file_add:000019760.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0203
16 |  | 19994 | 163.204 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:163.204,file:000019659.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
17 |  | 19994 | 1.2731 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:16,demand:1.27312,file_add:000019660.csv,file:NaN,load_type:heat,temperature:55
18 |  | 19994 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:16,demand:0.011,file:NaN,file_add:000019661.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
19 |  | 19994 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:16,demand:0.011,file:NaN,file_add:000019662.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
20 |  | 19994 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:16,demand:0.011,file:NaN,file_add:000019663.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
21 |  | 19994 | 0.0109 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:16,demand:0.0109,file_add:000019664.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0109
329 |  | 19849 | 49.9128 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:49.913,file:000020068.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
236 |  | 19767 | 153.9818 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:153.982,file:000019949.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
220 |  | 19761 | 104.8162 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:104.816,file:000019929.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
143 |  | 19686 | 78.6285 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:78.628,file:000019827.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
46 |  | 19522 | 155.4775 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:155.478,file:000019698.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
364 |  | 19414 | 266.0675 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:266.068,file:000020112.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
365 |  | 19414 | 0.73732 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:364,demand:0.73732,file_add:000020113.csv,file:NaN,load_type:heat,temperature:55
366 |  | 19414 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:364,demand:0.011,file:NaN,file_add:000020114.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
367 |  | 19414 | 0.0088 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:364,demand:0.0088,file_add:000020115.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0088
277 |  | 19288 | 292.4337 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:292.434,file:000020003.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
180 |  | 19210 | 208.8265 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:208.826,file:000019875.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
181 |  | 19210 | 0.67316 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:180,demand:0.6731600000000001,file_add:000019876.csv,file:NaN,load_type:heat,temperature:55
182 |  | 19210 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:180,demand:0.011,file:NaN,file_add:000019877.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
183 |  | 19210 | 0.0066 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:180,demand:0.0066,file_add:000019878.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0066
108 |  | 19147 | 110.6895 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:110.69,file:000019781.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
109 |  | 19147 | 0.46456 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:108,demand:0.46456,file_add:000019782.csv,file:NaN,load_type:heat,temperature:55
110 |  | 19147 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:108,demand:0.011,file:NaN,file_add:000019783.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
111 |  | 19147 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:108,demand:0.011,file:NaN,file_add:000019784.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
112 |  | 19147 | 0.0036 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:108,demand:0.0036,file_add:000019785.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0036
63 |  | 19040 | 226.7572 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:226.757,file:000019722.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
64 |  | 19040 | 0.99964 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:63,demand:0.9996400000000001,file_add:000019723.csv,file:NaN,load_type:heat,temperature:55
65 |  | 19040 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:63,demand:0.011,file:NaN,file_add:000019724.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
66 |  | 19040 | 0.0134 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:63,demand:0.0134,file_add:000019725.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0134
71 |  | 18552 | 204.1875 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:204.188,file:000019732.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
42 |  | 18493 | 200.9315 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:200.932,file:000019693.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
152 |  | 18160 | 87.9347 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:87.935,file:000019838.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
255 |  | 17736 | 54.6835 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:54.684,file:000019975.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
256 |  | 17736 | 0.76916 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:255,demand:0.7691600000000001,file_add:000019976.csv,file:NaN,load_type:heat,temperature:55
257 |  | 17736 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:255,demand:0.011,file:NaN,file_add:000019977.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
258 |  | 17736 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:255,demand:0.011,file:NaN,file_add:000019978.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
259 |  | 17736 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:255,demand:0.011,file:NaN,file_add:000019979.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
260 |  | 17736 | 0.0081 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:255,demand:0.0081,file_add:000019980.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0081
261 |  | 17231 | 69.7185 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:69.718,file:000019984.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
262 |  | 17231 | 0.76428 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:261,demand:0.76428,file_add:000019985.csv,file:NaN,load_type:heat,temperature:55
263 |  | 17231 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:261,demand:0.011,file:NaN,file_add:000019986.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
264 |  | 17231 | 0.0049 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:261,demand:0.0049,file_add:000019987.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0049
148 |  | 17130 | 161.3665 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:161.366,file:000019833.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
149 |  | 17130 | 0.81536 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:148,demand:0.8153600000000001,file_add:000019834.csv,file:NaN,load_type:heat,temperature:55
150 |  | 17130 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:148,demand:0.011,file:NaN,file_add:000019835.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
151 |  | 17130 | 0.0126 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:148,demand:0.0126,file_add:000019836.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0126
75 |  | 17042 | 132.4865 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:132.486,file:000019737.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
348 |  | 16829 | 23.4763 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:23.476,file:000020091.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
349 |  | 16829 | 1.0622 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:348,demand:1.0622,file_add:000020092.csv,file:NaN,load_type:heat,temperature:55
350 |  | 16829 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:348,demand:0.011,file:NaN,file_add:000020093.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
351 |  | 16829 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:348,demand:0.011,file:NaN,file_add:000020094.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
352 |  | 16829 | 0.0117 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:348,demand:0.0117,file_add:000020095.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0117
55 |  | 15953 | 99.658 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:99.658,file:000019711.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
56 |  | 15953 | 1.2499 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:55,demand:1.24988,file_add:000019712.csv,file:NaN,load_type:heat,temperature:55
57 |  | 15953 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:55,demand:0.011,file:NaN,file_add:000019713.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
58 |  | 15953 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:55,demand:0.011,file:NaN,file_add:000019714.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
59 |  | 15953 | 0.0134 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:55,demand:0.0134,file_add:000019715.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0134
0 |  | 15873 | 259.4583 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:259.458,file:000019638.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
1 |  | 15873 | 1.4593 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:0,demand:1.45932,file_add:000019639.csv,file:NaN,load_type:heat,temperature:55
2 |  | 15873 | 0.0099 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:0,demand:0.0099,file_add:000019640.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0099
386 |  | 15855 | 50.7338 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:50.734,file:000020143.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
387 |  | 15855 | 1.4991 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:386,demand:1.4991199999999998,file_add:000020144.csv,file:NaN,load_type:heat,temperature:55
388 |  | 15855 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:386,demand:0.011,file:NaN,file_add:000020145.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
389 |  | 15855 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:386,demand:0.011,file:NaN,file_add:000020146.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
390 |  | 15855 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:386,demand:0.011,file:NaN,file_add:000020147.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
391 |  | 15855 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:386,demand:0.011,file:NaN,file_add:000020148.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
392 |  | 15855 | 0.0102 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:386,demand:0.0102,file_add:000020149.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0102
310 |  | 15737 | 141.7865 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:141.786,file:000020044.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
311 |  | 15737 | 0.56032 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:310,demand:0.56032,file_add:000020045.csv,file:NaN,load_type:heat,temperature:55
312 |  | 15737 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:310,demand:0.011,file:NaN,file_add:000020046.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
313 |  | 15737 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:310,demand:0.011,file:NaN,file_add:000020047.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
314 |  | 15737 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:310,demand:0.011,file:NaN,file_add:000020048.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
315 |  | 15737 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:310,demand:0.011,file:NaN,file_add:000020049.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
316 |  | 15737 | 0.0063 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:310,demand:0.0063,file_add:000020050.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0063
117 |  | 15583 | 129.4737 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:129.474,file:000019792.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
118 |  | 15583 | 0.70124 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:117,demand:0.70124,file_add:000019793.csv,file:NaN,load_type:heat,temperature:55
119 |  | 15583 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:117,demand:0.011,file:NaN,file_add:000019794.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
120 |  | 15583 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:117,demand:0.011,file:NaN,file_add:000019795.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
121 |  | 15583 | 0.0068 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:117,demand:0.0068,file_add:000019796.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0068
166 |  | 14594 | 141.7865 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:141.786,file:000019857.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
167 |  | 14594 | 0.53652 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:166,demand:0.53652,file_add:000019858.csv,file:NaN,load_type:heat,temperature:55
168 |  | 14594 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:166,demand:0.011,file:NaN,file_add:000019859.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
169 |  | 14594 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:166,demand:0.011,file:NaN,file_add:000019860.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
170 |  | 14594 | 0.0035 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:166,demand:0.0035,file_add:000019861.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0035
122 |  | 14561 | 204.2072 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:204.207,file:000019800.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
123 |  | 14561 | 1.1607 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:122,demand:1.16072,file_add:000019801.csv,file:NaN,load_type:heat,temperature:55
124 |  | 14561 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:122,demand:0.011,file:NaN,file_add:000019802.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
125 |  | 14561 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:122,demand:0.011,file:NaN,file_add:000019803.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
126 |  | 14561 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:122,demand:0.011,file:NaN,file_add:000019804.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
127 |  | 14561 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:122,demand:0.011,file:NaN,file_add:000019805.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
128 |  | 14561 | 0.0107 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:122,demand:0.0107,file_add:000019806.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0107
240 |  | 14145 | 231.3123 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:231.312,file:000019957.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
215 |  | 14125 | 240.6848 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:240.685,file:000019923.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
206 |  | 14119 | 90.6195 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:90.62,file:000019910.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
207 |  | 14119 | 1.576 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:206,demand:1.57596,file_add:000019911.csv,file:NaN,load_type:heat,temperature:55
208 |  | 14119 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:206,demand:0.011,file:NaN,file_add:000019912.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
209 |  | 14119 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:206,demand:0.011,file:NaN,file_add:000019913.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
210 |  | 14119 | 0.0123 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:206,demand:0.0123,file_add:000019914.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0123
299 |  | 13668 | 120.612 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:120.612,file:000020031.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
300 |  | 13668 | 1.6224 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:299,demand:1.6224,file_add:000020032.csv,file:NaN,load_type:heat,temperature:55
301 |  | 13668 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:299,demand:0.011,file:NaN,file_add:000020033.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
302 |  | 13668 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:299,demand:0.011,file:NaN,file_add:000020034.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
303 |  | 13668 | 0.0066 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:299,demand:0.0066,file_add:000020035.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0066
368 |  | 13273 | 167.0083 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:167.008,file:000020117.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load
369 |  | 13273 | 1.8648 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:368,demand:1.8647599999999998,file_add:000020118.csv,file:NaN,load_type:heat,temperature:55
370 |  | 13273 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:368,demand:0.011,file:NaN,file_add:000020119.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
371 |  | 13273 | 0.011 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:368,demand:0.011,file:NaN,file_add:000020120.csv,cos_phi:0,load_type:ev,capacity:0.06,charging_home:0.011,charging_ac:0,charging_dc:0,efficiency:1.0,soc:0.5,v2g:False,v2h:False,load_type:ev
372 |  | 13273 | 0.0077 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,owner:368,demand:0.0077,file_add:000020121.csv,file:NaN,cos_phi:0.95,load_type:hp,power:0.0077
250 |  | 13127 | 109.35 | 0 | 0 | 0 |  | 1 | TRUE | wye | agent_type:sfh,dummy:False,demand:109.35,file:000019969.csv,file_add:NaN,cos_phi:1.0,load_type:inflexible-load

## sgen
Unnamed: 0 | name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source | description | sernum | for_name | chr_name
142 |  | 21274 | 0.014 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:189,power:0.014,file:000019894.csv,cos_phi:0.95,orientation:176,angle:60
143 |  | 21274 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:189,power:0.014,file:NaN,cos_phi:1,capacity:0.014,efficiency:0.96,soc:0.5,g2b:True,b2g:True
144 |  | 21274 | 0.426 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:189,power:0.426,capacity:0.2556,efficiency:0.9,soc:0.5
116 |  | 20723 | 0.0153 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:156,power:0.0153,file:000019851.csv,cos_phi:0.95,orientation:163,angle:51
117 |  | 20723 | 0.0007 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:156,power:0.0007,file:000019852.csv,cos_phi:0.95,orientation:343,angle:51
118 |  | 20723 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:156,power:0.016,file:NaN,cos_phi:1,capacity:0.016,efficiency:0.96,soc:0.5,g2b:True,b2g:True
119 |  | 20723 | 0.4192 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:156,power:0.4192,capacity:0.2516,efficiency:0.9,soc:0.5
182 |  | 20289 | 0.0081 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:245,power:0.0081,file:000019968.csv,cos_phi:0.95,orientation:266,angle:50
183 |  | 20289 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:245,power:0.0081,file:NaN,cos_phi:1,capacity:0.0081,efficiency:0.96,soc:0.5,g2b:True,b2g:True
184 |  | 20289 | 0.0554 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:245,power:0.0554,capacity:0.0332,efficiency:0.9,soc:0.5
68 |  | 20136 | 0.004 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:89,power:0.004,file:000019761.csv,cos_phi:0.95,orientation:-1,angle:90
69 |  | 20136 | 0.0124 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:89,power:0.0124,file:000019762.csv,cos_phi:0.95,orientation:269,angle:51
70 |  | 20136 | 0.0093 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:89,power:0.0093,file:000019763.csv,cos_phi:0.95,orientation:89,angle:51
71 |  | 20136 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:89,power:0.0257,file:NaN,cos_phi:1,capacity:0.0257,efficiency:0.96,soc:0.5,g2b:True,b2g:True
72 |  | 20136 | 0.3918 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:89,power:0.3918,capacity:0.2352,efficiency:0.9,soc:0.5
13 |  | 19994 | 0.0162 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:16,power:0.0162,file:000019665.csv,cos_phi:0.95,orientation:182,angle:46
14 |  | 19994 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:16,power:0.0162,file:NaN,cos_phi:1,capacity:0.0162,efficiency:0.96,soc:0.5,g2b:True,b2g:True
15 |  | 19994 | 0.2739 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:16,power:0.2739,capacity:0.1644,efficiency:0.9,soc:0.5
256 |  | 19414 | 0.0142 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:364,power:0.0142,file:000020116.csv,cos_phi:0.95,orientation:268,angle:49
257 |  | 19414 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:364,power:0.0142,file:NaN,cos_phi:1,capacity:0.0142,efficiency:0.96,soc:0.5,g2b:True,b2g:True
258 |  | 19414 | 0.4207 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:364,power:0.4207,capacity:0.2524,efficiency:0.9,soc:0.5
133 |  | 19210 | 0.012 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:180,power:0.012,file:000019879.csv,cos_phi:0.95,orientation:161,angle:45
134 |  | 19210 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:180,power:0.012,file:NaN,cos_phi:1,capacity:0.012,efficiency:0.96,soc:0.5,g2b:True,b2g:True
135 |  | 19210 | 0.198 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:180,power:0.198,capacity:0.1188,efficiency:0.9,soc:0.5
83 |  | 19147 | 0.0123 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:108,power:0.0123,file:000019786.csv,cos_phi:0.95,orientation:176,angle:50
84 |  | 19147 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:108,power:0.0123,file:NaN,cos_phi:1,capacity:0.0123,efficiency:0.96,soc:0.5,g2b:True,b2g:True
85 |  | 19147 | 0.1674 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:108,power:0.1674,capacity:0.1004,efficiency:0.9,soc:0.5
49 |  | 19040 | 0.0142 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:63,power:0.0142,file:000019726.csv,cos_phi:0.95,orientation:175,angle:50
50 |  | 19040 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:63,power:0.0142,file:NaN,cos_phi:1,capacity:0.0142,efficiency:0.96,soc:0.5,g2b:True,b2g:True
51 |  | 19040 | 0.2514 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:63,power:0.2514,capacity:0.1508,efficiency:0.9,soc:0.5
188 |  | 17736 | 0.0054 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:255,power:0.0054,file:000019981.csv,cos_phi:0.95,orientation:-1,angle:90
189 |  | 17736 | 0.015 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:255,power:0.015,file:000019982.csv,cos_phi:0.95,orientation:279,angle:43
190 |  | 17736 | 0.0028 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:255,power:0.0028,file:000019983.csv,cos_phi:0.95,orientation:99,angle:43
191 |  | 17736 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:255,power:0.0232,file:NaN,cos_phi:1,capacity:0.0232,efficiency:0.96,soc:0.5,g2b:True,b2g:True
192 |  | 17736 | 0.2752 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:255,power:0.2752,capacity:0.1652,efficiency:0.9,soc:0.5
193 |  | 17231 | 0.0102 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:261,power:0.0102,file:000019988.csv,cos_phi:0.95,orientation:178,angle:41
194 |  | 17231 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:261,power:0.0,file:NaN,cos_phi:1,capacity:0.0,efficiency:0.96,soc:0.5,g2b:True,b2g:True
195 |  | 17231 | 0.1266 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:261,power:0.1266,capacity:0.076,efficiency:0.9,soc:0.5
109 |  | 17130 | 0.0129 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:148,power:0.0129,file:000019837.csv,cos_phi:0.95,orientation:168,angle:71
110 |  | 17130 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:148,power:0.0,file:NaN,cos_phi:1,capacity:0.0,efficiency:0.96,soc:0.5,g2b:True,b2g:True
111 |  | 17130 | 0.3362 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:148,power:0.3362,capacity:0.2016,efficiency:0.9,soc:0.5
245 |  | 16829 | 0.0123 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:348,power:0.0123,file:000020096.csv,cos_phi:0.95,orientation:177,angle:52
246 |  | 16829 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:348,power:0.0123,file:NaN,cos_phi:1,capacity:0.0123,efficiency:0.96,soc:0.5,g2b:True,b2g:True
247 |  | 16829 | 0.2185 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:348,power:0.2185,capacity:0.1312,efficiency:0.9,soc:0.5
42 |  | 15953 | 0.0178 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:55,power:0.0178,file:000019716.csv,cos_phi:0.95,orientation:173,angle:55
43 |  | 15953 | 0.0008 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:55,power:0.0008,file:000019717.csv,cos_phi:0.95,orientation:353,angle:55
44 |  | 15953 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:55,power:0.0,file:NaN,cos_phi:1,capacity:0.0,efficiency:0.96,soc:0.5,g2b:True,b2g:True
45 |  | 15953 | 0.5501 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:55,power:0.5501,capacity:0.33,efficiency:0.9,soc:0.5
0 |  | 15873 | 0.0042 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:0,power:0.0042,file:000019641.csv,cos_phi:0.95,orientation:-1,angle:90
1 |  | 15873 | 0.0058 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:0,power:0.0058,file:000019642.csv,cos_phi:0.95,orientation:176,angle:57
2 |  | 15873 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:0,power:0.0,file:NaN,cos_phi:1,capacity:0.0,efficiency:0.96,soc:0.5,g2b:True,b2g:True
3 |  | 15873 | 0.3168 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:0,power:0.3168,capacity:0.19,efficiency:0.9,soc:0.5
273 |  | 15855 | 0.0204 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:386,power:0.0204,file:000020150.csv,cos_phi:0.95,orientation:178,angle:41
274 |  | 15855 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:386,power:0.0204,file:NaN,cos_phi:1,capacity:0.0204,efficiency:0.96,soc:0.5,g2b:True,b2g:True
275 |  | 15855 | 0.2865 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:386,power:0.2865,capacity:0.172,efficiency:0.9,soc:0.5
222 |  | 15737 | 0.0102 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:310,power:0.0102,file:000020051.csv,cos_phi:0.95,orientation:271,angle:41
223 |  | 15737 | 0.0062 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:310,power:0.0062,file:000020052.csv,cos_phi:0.95,orientation:91,angle:41
224 |  | 15737 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:310,power:0.0,file:NaN,cos_phi:1,capacity:0.0,efficiency:0.96,soc:0.5,g2b:True,b2g:True
225 |  | 15737 | 0.2436 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:310,power:0.2436,capacity:0.146,efficiency:0.9,soc:0.5
89 |  | 15583 | 0.0074 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:117,power:0.0074,file:000019797.csv,cos_phi:0.95,orientation:262,angle:65
90 |  | 15583 | 0.0064 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:117,power:0.0064,file:000019798.csv,cos_phi:0.95,orientation:352,angle:64
91 |  | 15583 | 0.004 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:117,power:0.004,file:000019799.csv,cos_phi:0.95,orientation:82,angle:65
92 |  | 15583 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:117,power:0.0,file:NaN,cos_phi:1,capacity:0.0,efficiency:0.96,soc:0.5,g2b:True,b2g:True
93 |  | 15583 | 0.1728 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:117,power:0.1728,capacity:0.1036,efficiency:0.9,soc:0.5
123 |  | 14594 | 0.011 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:166,power:0.011,file:000019862.csv,cos_phi:0.95,orientation:176,angle:39
124 |  | 14594 | 0.0003 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:166,power:0.011,file:NaN,cos_phi:1,capacity:0.011,efficiency:0.96,soc:0.5,g2b:True,b2g:True
125 |  | 14594 | 0.1417 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:166,power:0.1417,capacity:0.0852,efficiency:0.9,soc:0.5
94 |  | 14561 | 0.0106 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:122,power:0.0106,file:000019807.csv,cos_phi:0.95,orientation:267,angle:52
95 |  | 14561 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:122,power:0.0106,file:NaN,cos_phi:1,capacity:0.0106,efficiency:0.96,soc:0.5,g2b:True,b2g:True
96 |  | 14561 | 0.2851 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:122,power:0.2851,capacity:0.1712,efficiency:0.9,soc:0.5
152 |  | 14119 | 0.0046 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:206,power:0.0046,file:000019915.csv,cos_phi:0.95,orientation:-1,angle:90
153 |  | 14119 | 0.0106 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:206,power:0.0106,file:000019916.csv,cos_phi:0.95,orientation:170,angle:71
154 |  | 14119 | 0.0106 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:206,power:0.0106,file:000019917.csv,cos_phi:0.95,orientation:350,angle:71
155 |  | 14119 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:206,power:0.0258,file:NaN,cos_phi:1,capacity:0.0258,efficiency:0.96,soc:0.5,g2b:True,b2g:True
156 |  | 14119 | 0.3605 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:206,power:0.3605,capacity:0.2164,efficiency:0.9,soc:0.5
216 |  | 13668 | 0.0099 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:299,power:0.0099,file:000020036.csv,cos_phi:0.95,orientation:161,angle:60
217 |  | 13668 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:299,power:0.0099,file:NaN,cos_phi:1,capacity:0.0099,efficiency:0.96,soc:0.5,g2b:True,b2g:True
218 |  | 13668 | 0.2561 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:299,power:0.2561,capacity:0.1536,efficiency:0.9,soc:0.5
259 |  | 13273 | 0.0154 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:368,power:0.0154,file:000020122.csv,cos_phi:0.95,orientation:167,angle:50
260 |  | 13273 | 0.0011 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:pv,owner:368,power:0.0011,file:000020123.csv,cos_phi:0.95,orientation:347,angle:50
261 |  | 13273 | 0 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:battery,owner:368,power:0.0,file:NaN,cos_phi:1,capacity:0.0,efficiency:0.96,soc:0.5,g2b:True,b2g:True
262 |  | 13273 | 0.2066 | 0 |  | 1 | TRUE | wye | TRUE | plant_type:heat-storage,owner:368,power:0.2066,capacity:0.124,efficiency:0.9,soc:0.5

## switch
| bus | element | et | type | closed | name | z_ohm | in_ka
236 | 21962 | 23924 | l | CB | TRUE |  | 0
973 | 21962 | 28035 | l | CB | TRUE |  | 0
1224 | 21688 | 29486 | l | CB | TRUE |  | 0
1408 | 21962 | 30319 | l | CB | TRUE |  | 0
1787 | 21688 | 32301 | l | CB | TRUE |  | 0
2231 | 22455 | 33650 | l | CB | TRUE |  | 0
2479 | 22455 | 33996 | l | CB | TRUE |  | 0

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service | s_sc_max_mva | s_sc_min_mva | rx_min | rx_max | r0x0_max | x0x_max | r0x0_min | x0x_min | description
0 | 3068068_000165 | 22454 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km | alpha | temperature_degree_celsius | description | line_idx | folder_id | section_idx
12944 | 7068068_001001_005005_00040005_06002 | NYY-J 4x35 | 22621 | 19156 | 0.029 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 12944 | SWF | 0
13193 | 7068068_001001_004004_00160017_06001 | NYY-J 4x35 | 22864 | 15583 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13193 | SWF | 0
13352 | 7068068_001001_005005_00660067_06001 | NAYY-J 4x50 | 23025 | 14125 | 0.017 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 13352 | SWF | 0
13353 | 7068068_001001_005005_00450046_06001 | NYY-J 4x35 | 23026 | 23027 | 0.009 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13353 | SWF | 0
13423 | 7068068_001001_001001_00010002_06002 | NYY 4x10 | 23093 | 19423 | 0.001 | 1.8303 | 0.094562 | 0 | 0 | 0.075 | 1 | 1 | cs | TRUE | 7.3214 | 0.37825 | 0 | 0.00393 | 70 |  | 13423 | SWF | 0
13469 | 7068068_001001_005005_00380040_06001 | NYY-J 4x35 | 23140 | 20997 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13469 | SWF | 0
13559 | 7068068_001001_005005_00140015_06002 | NYY-J 4x35 | 23229 | 19210 | 0.008 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13559 | SWF | 0
13599 | 7068068_001001_005005_00960097_06001 | NYY-J 4x35 | 23269 | 18160 | 0.039 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13599 | SWF | 0
13662 | 7068068_001001_003003_00120016_06001 | NYY-J 4x35 | 23333 | 14119 | 0.032 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13662 | SWF | 0
13752 | 7068068_001001_004004_00240025_06001 | NYY-J 4x35 | 23421 | 21249 | 0.021 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13752 | SWF | 0
13866 | 7068068_001001_005005_00220026_06001 | NYY-J 4x35 | 23529 | 23530 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13866 | SWF | 0
13879 | 7068068_001001_003003_00080009_06001 | NYY-J 4x35 | 23545 | 19100 | 0.016 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 13879 | SWF | 0
14007 | 7068068_001001_005005_01080109_06001 | NYY-J 4x35 | 23675 | 19791 | 0.016 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14007 | SWF | 0
14046 | 7068068_001001_005005_00380041_06001 | NYY-J 4x35 | 23140 | 17759 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14046 | SWF | 0
14102 | 7068068_001001_005005_00180019_06003 | NYY-J 4x35 | 23774 | 13757 | 0.019 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14102 | SWF | 0
14139 | 7068068_001001_005005_00820083_06001 | NYY-J 4x35 | 23810 | 19255 | 0.019 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14139 | SWF | 0
14185 | 7068068_001001_005005_00290030_06001 | NYY-J 4x35 | 23853 | 16217 | 0.017 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14185 | SWF | 0
14345 | 7068068_001001_005005_00020003_06001 | NYY-J 4x35 | 24006 | 24007 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14345 | SWF | 0
14360 | 7068068_001001_005005_00700071_06001 | NYY-J 4x35 | 24023 | 21292 | 0.015 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14360 | SWF | 0
14515 | 7068068_001001_004004_00180019_06001 | NYY-J 4x35 | 24173 | 13798 | 0.036 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14515 | SWF | 0
14591 | 7068068_001001_002002_00010002_06002 | NAYY-J 4x50 | 24246 | 24247 | 0.106 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 14591 | SWF | 0
14732 | 7068068_001001_005005_00390042_06001 | NYY-J 4x35 | 24384 | 24385 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14732 | SWF | 0
14759 | 7068068_001001_005005_00580059_06001 | NAYY-J 4x50 | 24409 | 18209 | 0.016 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 14759 | SWF | 0
14790 | 7068068_001001_005005_00210024_06001 | NYY-J 4x35 | 24441 | 17130 | 0.011 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14790 | SWF | 0
14956 | 7068068_001001_005005_00230055_06001 | NYY-J 4x35 | 24593 | 20521 | 0.012 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 14956 | SWF | 0
15026 | 7068068_001001_003003_00060007_06001 | NYY-J 4x35 | 24658 | 13509 | 0.01 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15026 | SWF | 0
15064 | 7068068_001001_004004_00140015_06001 | NYY-J 4x35 | 24696 | 20289 | 0.028 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15064 | SWF | 0
15107 | 7068068_001001_005005_00160017_06001 | NYY-J 4x35 | 24742 | 24743 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15107 | SWF | 0
15156 | 7068068_001001_005005_01020103_06001 | NYY-J 4x35 | 24786 | 14447 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15156 | SWF | 0
15235 | 7068068_001001_005005_00390042_06002 | NYY-J 4x35 | 24384 | 15888 | 0.015 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15235 | SWF | 0
15240 | 7068068_001001_005005_00060007_06002 | NYY-J 4x35 | 24866 | 19101 | 0.008 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15240 | SWF | 0
15305 | 7068068_001001_004004_00120013_06001 | NYY-J 4x35 | 24919 | 14321 | 0.019 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15305 | SWF | 0
15323 | 7068068_001001_005005_01150117_06001 | NYY-J 4x35 | 24940 | 15784 | 0.033 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15323 | SWF | 0
15341 | 7068068_001001_005005_00780079_06001 | NYY-J 4x35 | 24958 | 15953 | 0.012 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15341 | SWF | 0
15349 | 7068068_001001_005005_00040005_06001 | NYY-J 4x35 | 24965 | 22621 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15349 | SWF | 0
15350 | 7068068_001001_005005_00560057_06001 | NYY-J 4x35 | 24966 | 17042 | 0.014 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15350 | SWF | 0
15433 | 7068068_001001_005005_00350036_06001 | NYY-J 4x35 | 25044 | 15884 | 0.034 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15433 | SWF | 0
15729 | 7068068_001001_004004_00280029_06001 | NYY-J 4x35 | 25331 | 19040 | 0.008 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 15729 | SWF | 0
16000 | 7068068_001001_005005_00120013_06002 | NYY-J 4x35 | 25587 | 20008 | 0.005 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 16000 | SWF | 0
16084 | 7068068_001001_005005_00900091_06001 | NYY-J 4x35 | 25671 | 13172 | 0.015 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 16084 | SWF | 0
16286 | 7068068_001001_005005_01040105_06001 | NYY-J 4x35 | 25867 | 17231 | 0.021 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 16286 | SWF | 0
16308 | 7068068_001001_004004_00200021_06001 | NYY 4x10 | 25886 | 21443 | 0.009 | 1.8303 | 0.094562 | 0 | 0 | 0.075 | 1 | 1 | cs | TRUE | 7.3214 | 0.37825 | 0 | 0.00393 | 70 |  | 16308 | SWF | 0
16309 | 7068068_001001_005005_00020003_06002 | NYY-J 4x35 | 24007 | 18552 | 0.021 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 16309 | SWF | 0
17295 | 7068068_001001_005005_00760077_06001 | NYY-J 4x35 | 26780 | 14561 | 0.019 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17295 | SWF | 0
17377 | 7068068_001001_005005_00220026_06002 | NYY-J 4x35 | 23529 | 19288 | 0.015 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17377 | SWF | 0
17456 | 7068068_001001_003003_00040005_06001 | NAYY-J 4x50 | 21688 | 19279 | 0.019 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 17456 | SWF | 0
17572 | 7068068_001001_005005_00600061_06001 | NYY-J 4x35 | 27031 | 19767 | 0.017 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17572 | SWF | 0
17608 | 7068068_001001_004004_00080009_06001 | NYY-J 4x35 | 27063 | 19522 | 0.039 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17608 | SWF | 0
17686 | 7068068_001001_005005_00140015_06001 | NYY-J 4x35 | 27134 | 23229 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17686 | SWF | 0
17728 | 7068068_001001_004004_00040005_06001 | NYY-J 4x35 | 27169 | 13273 | 0.035 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17728 | SWF | 0
17952 | 7068068_001001_003003_00140015_06001 | NYY-J 4x35 | 27379 | 13668 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17952 | SWF | 0
17993 | 7068068_001001_002002_00010002_06003 | NYY-J 4x35 | 24247 | 20074 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 17993 | SWF | 0
18048 | 7068068_001001_005005_00860087_06001 | NYY-J 4x35 | 27461 | 15617 | 0.012 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18048 | SWF | 0
18206 | 7068068_001001_005005_00470048_06001 | NYY-J 4x35 | 27613 | 27614 | 0.005 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18206 | SWF | 0
18313 | 7068068_001001_005005_00490050_06002 | NYY-J 4x35 | 27709 | 19849 | 0.009 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18313 | SWF | 0
18343 | 7068068_001001_005005_00310032_06001 | NYY-J 4x35 | 27738 | 15293 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18343 | SWF | 0
18378 | 7068068_001001_005005_01000101_06001 | NYY-J 4x35 | 27767 | 14594 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18378 | SWF | 0
18409 | 7068068_001001_005005_00840085_06001 | NYY-J 4x35 | 27793 | 13368 | 0.016 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18409 | SWF | 0
18540 | 7068068_001001_005005_00080009_06002 | NYY-J 4x35 | 27906 | 19147 | 0.029 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18540 | SWF | 0
18654 | 7068068_001001_005005_00270028_06001 | NYY-J 4x35 | 28011 | 19994 | 0.017 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18654 | SWF | 0
18695 | 7068068_001001_005005_00530054_06002 | NYY-J 4x35 | 28045 | 17736 | 0.005 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18695 | SWF | 0
18775 | 7068068_001001_005005_00800081_06001 | NYY-J 4x35 | 28114 | 19761 | 0.012 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18775 | SWF | 0
18796 | 7068068_001001_005005_00060007_06001 | NYY-J 4x35 | 28134 | 24866 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18796 | SWF | 0
18891 | 7068068_001001_005005_00940095_06001 | NYY-J 4x35 | 28205 | 21274 | 0.014 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18891 | SWF | 0
18925 | 7068068_001001_004004_00260027_06001 | NYY-J 4x35 | 28230 | 16058 | 0.028 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 18925 | SWF | 0
19091 | 7068068_001001_005005_00740075_06001 | NYY-J 4x35 | 28365 | 13662 | 0.025 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19091 | SWF | 0
19400 | 7068068_001001_005005_00180019_06002 | NAYY-J 4x50 | 28628 | 23774 | 0.019 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 19400 | SWF | 0
19464 | 7068068_001001_005005_01120113_06001 | NYY-J 4x35 | 28680 | 15855 | 0.016 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19464 | SWF | 0
19632 | 7068068_001001_005005_00720073_06001 | NYY-J 4x35 | 28832 | 19414 | 0.012 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19632 | SWF | 0
19654 | 7068068_001001_005005_00120013_06001 | NYY-J 4x35 | 28850 | 25587 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19654 | SWF | 0
19655 | 7068068_001001_005005_00330034_06002 | NYY-J 4x35 | 28851 | 15873 | 0.016 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19655 | SWF | 0
19709 | 7068068_001001_005005_00430044_06002 | NYY-J 4x35 | 28898 | 21071 | 0.01 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 19709 | SWF | 0
20027 | 7068068_001001_003003_00020003_06001 | NAYY-J 4x50 | 29177 | 16644 | 0.023 | 0.641 | 0.084823 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 2.564 | 0.33929 | 0 | 0 | 70 |  | 20027 | SWF | 0
20102 | 7068068_001001_005005_00880089_06001 | NYY-J 4x35 | 29239 | 20770 | 0.022 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20102 | SWF | 0
20211 | 7068068_001001_005005_00180019_06001 | NYY-J 4x35 | 29332 | 28628 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20211 | SWF | 0
20310 | 7068068_001001_005005_00920093_06001 | NYY-J 4x35 | 29414 | 16423 | 0.018 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20310 | SWF | 0
20373 | 7068068_001001_005005_00510052_06001 | NYY-J 4x35 | 29465 | 29466 | 0.001 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20373 | SWF | 0
20383 | 7068068_001001_005005_00430044_06001 | NYY-J 4x35 | 28898 | 29476 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20383 | SWF | 0
20456 | 7068068_001001_004004_00220023_06001 | NYY-J 4x35 | 29540 | 20136 | 0.009 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20456 | SWF | 0
20457 | 7068068_001001_005005_00980099_06001 | NYY-J 4x35 | 29541 | 16765 | 0.017 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20457 | SWF | 0
20489 | 7068068_001001_005005_00450046_06002 | NYY-J 4x35 | 23026 | 17208 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20489 | SWF | 0
20546 | 7068068_001001_005005_00330034_06001 | NYY-J 4x35 | 29618 | 28851 | 0.002 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20546 | SWF | 0
20574 | 7068068_001001_003003_00110013_06001 | NYY-J 4x35 | 29641 | 20723 | 0.008 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20574 | SWF | 0
20641 | 7068068_001001_005005_01060107_06001 | NYY-J 4x35 | 29701 | 20561 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20641 | SWF | 0
20678 | 7068068_001001_003003_00170018_06001 | NYY-J 4x35 | 29734 | 20968 | 0.029 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20678 | SWF | 0
20975 | 7068068_001001_005005_00510052_06002 | NYY-J 4x35 | 29465 | 15737 | 0.01 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20975 | SWF | 0
20991 | 7068068_001001_004004_00020003_06001 | NYY-J 4x35 | 29999 | 18493 | 0.023 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 20991 | SWF | 0
21052 | 7068068_001001_005005_00530054_06001 | NYY-J 4x35 | 30041 | 28045 | 0.006 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 21052 | SWF | 0
21076 | 7068068_001001_005005_00100011_06001 | NYY-J 4x35 | 30063 | 21166 | 0.02 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 21076 | SWF | 0
21110 | 7068068_001001_005005_00160017_06002 | NYY-J 4x35 | 24742 | 13127 | 0.018 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 21110 | SWF | 0
21619 | 7068068_001001_005005_00490050_06001 | NYY-J 4x35 | 30513 | 27709 | 0.004 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 21619 | SWF | 0
21907 | 7068068_001001_005005_00470048_06002 | NYY-J 4x35 | 27613 | 16101 | 0.006 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 21907 | SWF | 0
22043 | 7068068_001001_003003_00170019_06001 | NYY-J 4x35 | 29734 | 19216 | 0.018 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22043 | SWF | 0
22169 | 7068068_001001_005005_01150118_06001 | NYY-J 4x35 | 24940 | 16829 | 0.003 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22169 | SWF | 0
22322 | 7068068_001001_004004_00100011_06001 | NYY-J 4x35 | 31058 | 14145 | 0.04 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22322 | SWF | 0
22411 | 7068068_001001_004004_00060007_06001 | NYY-J 4x35 | 31130 | 19686 | 0.006 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22411 | SWF | 0
22460 | 7068068_001001_005005_00680069_06001 | NYY-J 4x50 | 31166 | 20868 | 0.016 | 0.38696 | 0.084823 | 0 | 0 | 0.185 | 1 | 1 | cs | TRUE | 1.5478 | 0.33929 | 0 | 0.00393 | 70 |  | 22460 | SWF | 0
22569 | 7068068_001001_005005_00630065_06001 | NYY-J 4x35 | 31269 | 20420 | 0.009 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22569 | SWF | 0
22619 | 7068068_001001_005005_01100111_06001 | NYY-J 4x35 | 31305 | 17124 | 0.008 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22619 | SWF | 0
22714 | 7068068_001001_005005_00080009_06001 | NYY-J 4x35 | 31372 | 27906 | 0.004 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 22714 | SWF | 0
22830 | 7068068_001001_003003_00110014_06001 | NYY-J 4x120 | 27379 | 29641 | 0.017 | 0.15378 | 0.080425 | 0 | 0 | 0.313 | 1 | 1 | cs | TRUE | 0.61513 | 0.3217 | 0 | 0.00393 | 70 |  | 22830 | SWF | 0
22831 | 7068068_001001_003003_00100011_06001 | NYY-J 4x120 | 29641 | 31418 | 0.01 | 0.15378 | 0.080425 | 0 | 0 | 0.313 | 1 | 1 | cs | TRUE | 0.61513 | 0.3217 | 0 | 0.00393 | 70 |  | 22831 | SWF | 0
23924 | 7068068_001001_005005_00180020_06002 | NAYY 4x185SE 0.6/1kV | 31845 | 21962 | 0.081 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 23924 | SWF | 0
24217 | 7068068_001001_005005_00210025_06001 | NYY-J 3x95SM 0.6/1kV | 31950 | 24441 | 0.004 | 0.1941 | 0.07477 | 1160 | 0 | 0.332 | 1 | 1 | cs | TRUE | 0.7766 | 0.29908 | 496.2 | 0.00393 | 70 |  | 24217 | SWF | 0
24218 | 7068068_001001_005005_00200021_06001 | NYY-J 3x95SM 0.6/1kV | 24441 | 21962 | 0.023 | 0.1941 | 0.07477 | 1160 | 0 | 0.332 | 1 | 1 | cs | TRUE | 0.7766 | 0.29908 | 496.2 | 0.00393 | 70 |  | 24218 | SWF | 0
24230 | 7068068_001001_003003_00010002_06002 | NAYY 4x120SE 0.6/1kV | 31952 | 31953 | 0.007 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 24230 | SWF | 0
26673 | 7068068_001001_005005_00370038_06001 | NYY-J 4x35 | 32664 | 23140 | 0.01 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 26673 | SWF | 0
28035 | 7068068_001001_005005_00200022_06001 | NAYY 4x185SE 0.6/1kV | 21962 | 23530 | 0.056 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28035 | SWF | 0
28036 | 7068068_001001_005005_00220027_06001 | NAYY 4x185SE 0.6/1kV | 23530 | 28011 | 0.013 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28036 | SWF | 0
28037 | 7068068_001001_005005_00270029_06001 | NAYY 4x185SE 0.6/1kV | 28011 | 23853 | 0.01 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28037 | SWF | 0
28038 | 7068068_001001_005005_00290031_06001 | NAYY 4x185SE 0.6/1kV | 23853 | 27738 | 0.022 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28038 | SWF | 0
28039 | 7068068_001001_005005_00310033_06001 | NAYY 4x185SE 0.6/1kV | 27738 | 29618 | 0.004 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28039 | SWF | 0
28040 | 7068068_001001_005005_00330035_06001 | NAYY 4x185SE 0.6/1kV | 29618 | 25044 | 0.023 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28040 | SWF | 0
28041 | 7068068_001001_005005_00350037_06001 | NAYY 4x185SE 0.6/1kV | 25044 | 32664 | 0.02 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28041 | SWF | 0
28042 | 7068068_001001_005005_00370039_06001 | NAYY 4x185SE 0.6/1kV | 32664 | 24385 | 0.001 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28042 | SWF | 0
28043 | 7068068_001001_005005_00390043_06001 | NAYY 4x185SE 0.6/1kV | 24385 | 29476 | 0.028 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28043 | SWF | 0
28044 | 7068068_001001_005005_00430045_06001 | NAYY 4x185SE 0.6/1kV | 29476 | 23027 | 0.002 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28044 | SWF | 0
28045 | 7068068_001001_005005_00450047_06001 | NAYY 4x185SE 0.6/1kV | 23027 | 27614 | 0.022 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28045 | SWF | 0
28046 | 7068068_001001_005005_00470049_06001 | NAYY 4x185SE 0.6/1kV | 27614 | 30513 | 0.018 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28046 | SWF | 0
28047 | 7068068_001001_005005_00490051_06001 | NAYY 4x185SE 0.6/1kV | 30513 | 29466 | 0.031 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28047 | SWF | 0
28048 | 7068068_001001_005005_00510053_06001 | NAYY 4x185SE 0.6/1kV | 29466 | 30041 | 0.034 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28048 | SWF | 0
28082 | 7068068_001001_003003_00100012_06001 | NYY-J 4x35 | 31418 | 23333 | 0.007 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 28082 | SWF | 0
28083 | 7068068_001001_003003_00120017_06001 | NYY-J 4x35 | 23333 | 29734 | 0.014 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 28083 | SWF | 0
28905 | 7068068_001001_005005_01120114_06001 | NYY-J 3x70SM 0.6/1kV | 33090 | 28680 | 0.002 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28905 | SWF | 0
28906 | 7068068_001001_005005_01100112_06001 | NYY-J 3x70SM 0.6/1kV | 28680 | 31305 | 0.001 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28906 | SWF | 0
28907 | 7068068_001001_005005_01080110_06001 | NYY-J 3x70SM 0.6/1kV | 31305 | 23675 | 0.015 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28907 | SWF | 0
28908 | 7068068_001001_005005_01060108_06001 | NYY-J 3x70SM 0.6/1kV | 23675 | 29701 | 0.007 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28908 | SWF | 0
28909 | 7068068_001001_005005_01040106_06001 | NYY-J 3x70SM 0.6/1kV | 29701 | 25867 | 0.022 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28909 | SWF | 0
28910 | 7068068_001001_005005_01020104_06001 | NYY-J 3x70SM 0.6/1kV | 25867 | 24786 | 0.002 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28910 | SWF | 0
28911 | 7068068_001001_005005_01000102_06001 | NYY-J 3x70SM 0.6/1kV | 24786 | 27767 | 0.008 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28911 | SWF | 0
28912 | 7068068_001001_005005_00980100_06003 | NYY-J 3x70SM 0.6/1kV | 27767 | 33142 | 0.001 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 28912 | SWF | 0
28956 | 7068068_001001_004004_00010002_06002 | NAYY 4x120SE 0.6/1kV | 33148 | 29999 | 0.04 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28956 | SWF | 0
28957 | 7068068_001001_004004_00020004_06001 | NAYY 4x120SE 0.6/1kV | 29999 | 27169 | 0.005 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28957 | SWF | 0
28958 | 7068068_001001_004004_00040006_06001 | NAYY 4x120SE 0.6/1kV | 27169 | 31130 | 0.043 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28958 | SWF | 0
28959 | 7068068_001001_004004_00060008_06001 | NAYY 4x120SE 0.6/1kV | 31130 | 27063 | 0.007 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28959 | SWF | 0
28960 | 7068068_001001_004004_00080010_06001 | NAYY 4x120SE 0.6/1kV | 27063 | 31058 | 0.006 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28960 | SWF | 0
28961 | 7068068_001001_004004_00100012_06001 | NAYY 4x120SE 0.6/1kV | 31058 | 24919 | 0.013 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28961 | SWF | 0
28962 | 7068068_001001_004004_00120014_06001 | NAYY 4x120SE 0.6/1kV | 24919 | 24696 | 0.016 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28962 | SWF | 0
28963 | 7068068_001001_004004_00140016_06001 | NAYY 4x120SE 0.6/1kV | 24696 | 22864 | 0.002 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28963 | SWF | 0
28964 | 7068068_001001_004004_00160018_06001 | NAYY 4x120SE 0.6/1kV | 22864 | 24173 | 0.023 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28964 | SWF | 0
28965 | 7068068_001001_004004_00180020_06001 | NAYY 4x120SE 0.6/1kV | 24173 | 25886 | 0.001 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28965 | SWF | 0
28966 | 7068068_001001_004004_00200022_06001 | NAYY 4x120SE 0.6/1kV | 25886 | 29540 | 0.051 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28966 | SWF | 0
28967 | 7068068_001001_004004_00220024_06001 | NAYY 4x120SE 0.6/1kV | 29540 | 23421 | 0.007 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28967 | SWF | 0
28968 | 7068068_001001_004004_00240026_06001 | NAYY 4x120SE 0.6/1kV | 23421 | 28230 | 0.021 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28968 | SWF | 0
28969 | 7068068_001001_004004_00260028_06001 | NAYY 4x120SE 0.6/1kV | 28230 | 25331 | 0.009 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28969 | SWF | 0
28970 | 7068068_001001_004004_00280030_06001 | NAYY 4x120SE 0.6/1kV | 25331 | 33149 | 0.022 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 28970 | SWF | 0
29366 | 7068068_001001_005005_00980100_06002 | NYY-J 3x70SM 0.6/1kV | 33220 | 33142 | 0.002 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 29366 | SWF | 0
29484 | 7068068_001001_003003_00080010_06001 | NYY-J 4x120 | 31418 | 23545 | 0.014 | 0.15378 | 0.080425 | 0 | 0 | 0.313 | 1 | 1 | cs | TRUE | 0.61513 | 0.3217 | 0 | 0.00393 | 70 |  | 29484 | SWF | 0
29485 | 7068068_001001_003003_00060008_06001 | NYY-J 4x120 | 23545 | 24658 | 0.038 | 0.15378 | 0.080425 | 0 | 0 | 0.313 | 1 | 1 | cs | TRUE | 0.61513 | 0.3217 | 0 | 0.00393 | 70 |  | 29485 | SWF | 0
29486 | 7068068_001001_003003_00040006_06001 | NYY-J 4x120 | 24658 | 21688 | 0.051 | 0.15378 | 0.080425 | 0 | 0 | 0.313 | 1 | 1 | cs | TRUE | 0.61513 | 0.3217 | 0 | 0.00393 | 70 |  | 29486 | SWF | 0
29708 | 7068068_001001_005005_00640115_06001 | NYY-J 4x35 | 33286 | 24940 | 0.015 | 0.52403 | 0.085137 | 0 | 0 | 0.156 | 1 | 1 | cs | TRUE | 2.0961 | 0.34055 | 0 | 0.00393 | 70 |  | 29708 | SWF | 0
30005 | 7068068_001001_005005_00010002_06002 | NAYY 4x185SE 0.6/1kV | 33342 | 24006 | 0.007 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30005 | SWF | 0
30006 | 7068068_001001_005005_00020004_06001 | NAYY 4x185SE 0.6/1kV | 24006 | 24965 | 0.011 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30006 | SWF | 0
30007 | 7068068_001001_005005_00040006_06001 | NAYY 4x185SE 0.6/1kV | 24965 | 28134 | 0.016 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30007 | SWF | 0
30008 | 7068068_001001_005005_00060008_06001 | NAYY 4x185SE 0.6/1kV | 28134 | 31372 | 0.007 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30008 | SWF | 0
30009 | 7068068_001001_005005_00080010_06001 | NAYY 4x185SE 0.6/1kV | 31372 | 30063 | 0.025 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30009 | SWF | 0
30010 | 7068068_001001_005005_00100012_06001 | NAYY 4x185SE 0.6/1kV | 30063 | 28850 | 0.001 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30010 | SWF | 0
30011 | 7068068_001001_005005_00120014_06001 | NAYY 4x185SE 0.6/1kV | 28850 | 27134 | 0.024 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30011 | SWF | 0
30012 | 7068068_001001_005005_00140016_06001 | NAYY 4x185SE 0.6/1kV | 27134 | 24743 | 0.002 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30012 | SWF | 0
30013 | 7068068_001001_005005_00160018_06001 | NAYY 4x185SE 0.6/1kV | 24743 | 29332 | 0.013 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30013 | SWF | 0
30014 | 7068068_001001_005005_00180020_06001 | NAYY 4x185SE 0.6/1kV | 29332 | 31845 | 0.001 | 0.165 | 0.080425 | 830 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0.66 | 0.3217 | 385.9 | 0.00403 | 70 |  | 30014 | SWF | 0
30315 | 7068068_001001_005005_00600062_06001 | NYY-J 3x70SM 0.6/1kV | 33388 | 27031 | 0.017 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30315 | SWF | 0
30316 | 7068068_001001_005005_00580060_06001 | NYY-J 3x70SM 0.6/1kV | 27031 | 24409 | 0.005 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30316 | SWF | 0
30317 | 7068068_001001_005005_00560058_06001 | NYY-J 3x70SM 0.6/1kV | 24409 | 24966 | 0.014 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30317 | SWF | 0
30318 | 7068068_001001_005005_00230056_06001 | NYY-J 3x70SM 0.6/1kV | 24966 | 24593 | 0.012 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30318 | SWF | 0
30319 | 7068068_001001_005005_00200023_06001 | NYY-J 3x70SM 0.6/1kV | 24593 | 21962 | 0.054 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30319 | SWF | 0
30894 | 7068068_001001_005005_00980100_06001 | NYY-J 3x70SM 0.6/1kV | 33220 | 29541 | 0.001 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30894 | SWF | 0
30895 | 7068068_001001_005005_00960098_06001 | NYY-J 3x70SM 0.6/1kV | 29541 | 23269 | 0.007 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30895 | SWF | 0
30896 | 7068068_001001_005005_00940096_06001 | NYY-J 3x70SM 0.6/1kV | 23269 | 28205 | 0.002 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30896 | SWF | 0
30897 | 7068068_001001_005005_00920094_06001 | NYY-J 3x70SM 0.6/1kV | 28205 | 29414 | 0.018 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30897 | SWF | 0
30898 | 7068068_001001_005005_00900092_06001 | NYY-J 3x70SM 0.6/1kV | 29414 | 25671 | 0.007 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30898 | SWF | 0
30899 | 7068068_001001_005005_00880090_06001 | NYY-J 3x70SM 0.6/1kV | 25671 | 29239 | 0.001 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30899 | SWF | 0
30900 | 7068068_001001_005005_00860088_06001 | NYY-J 3x70SM 0.6/1kV | 29239 | 27461 | 0.018 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30900 | SWF | 0
30901 | 7068068_001001_005005_00840086_06001 | NYY-J 3x70SM 0.6/1kV | 27461 | 27793 | 0.002 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30901 | SWF | 0
30902 | 7068068_001001_005005_00820084_06001 | NYY-J 3x70SM 0.6/1kV | 27793 | 23810 | 0.022 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30902 | SWF | 0
30903 | 7068068_001001_005005_00800082_06001 | NYY-J 3x70SM 0.6/1kV | 23810 | 28114 | 0.003 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30903 | SWF | 0
30904 | 7068068_001001_005005_00780080_06001 | NYY-J 3x70SM 0.6/1kV | 28114 | 24958 | 0.018 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30904 | SWF | 0
30905 | 7068068_001001_005005_00760078_06001 | NYY-J 3x70SM 0.6/1kV | 24958 | 26780 | 0.001 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30905 | SWF | 0
30906 | 7068068_001001_005005_00740076_06001 | NYY-J 3x70SM 0.6/1kV | 26780 | 28365 | 0.013 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30906 | SWF | 0
30907 | 7068068_001001_005005_00720074_06001 | NYY-J 3x70SM 0.6/1kV | 28365 | 28832 | 0.01 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30907 | SWF | 0
30908 | 7068068_001001_005005_00700072_06001 | NYY-J 3x70SM 0.6/1kV | 28832 | 24023 | 0.019 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30908 | SWF | 0
30909 | 7068068_001001_005005_00680070_06001 | NYY-J 3x70SM 0.6/1kV | 24023 | 31166 | 0.004 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30909 | SWF | 0
30910 | 7068068_001001_005005_00660068_06001 | NYY-J 3x70SM 0.6/1kV | 31166 | 23025 | 0.013 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30910 | SWF | 0
30911 | 7068068_001001_005005_00630066_06001 | NYY-J 3x70SM 0.6/1kV | 23025 | 31269 | 0.009 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30911 | SWF | 0
30912 | 7068068_001001_005005_00620063_06001 | NYY-J 3x70SM 0.6/1kV | 31269 | 33388 | 0.03 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 30912 | SWF | 0
31375 | 7068068_001001_005005_00620064_06001 | NYY-J 3x70SM 0.6/1kV | 33388 | 33286 | 0.016 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31375 | SWF | 0
31376 | 7068068_001001_005005_00640116_06001 | NYY-J 3x70SM 0.6/1kV | 33286 | 33520 | 0.026 | 0.2686 | 0.07477 | 1130 | 0 | 0.276 | 1 | 1 | cs | TRUE | 1.0745 | 0.29908 | 477.8 | 0.00393 | 70 |  | 31376 | SWF | 0
32300 | 7068068_001001_003003_00010002_06003 | NAYY 4x120SE 0.6/1kV | 31953 | 29177 | 0.026 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 32300 | SWF | 0
32301 | 7068068_001001_003003_00020004_06001 | NAYY 4x120SE 0.6/1kV | 29177 | 21688 | 0.076 | 0.2542 | 0.080425 | 840 | 0 | 0.24 | 1 | 1 | cs | TRUE | 1.0167 | 0.3217 | 385.9 | 0.00403 | 70 |  | 32301 | SWF | 0
33066 | 7068068_001001_001001_00010002_06001 | NS-Leitungstyp_fiktiv | 23093 | 22455 | 0.001 | 0 | 0 | 0 | 0 | 0.075 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 33066 | SWF | 0
33126 | 7068068_001001_002002_00010002_06001 | NS-Leitungstyp_fiktiv | 24246 | 22455 | 0.003 | 0 | 0 | 0 | 0 | 0.144 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 33126 | SWF | 0
33650 | 7068068_001001_003003_00010002_06001 | NS-Leitungstyp_fiktiv | 31952 | 22455 | 0.002 | 0 | 0 | 0 | 0 | 0.24 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 33650 | SWF | 0
33921 | 7068068_001001_004004_00010002_06001 | NS-Leitungstyp_fiktiv | 33148 | 22455 | 0.001 | 0 | 0 | 0 | 0 | 0.24 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 33921 | SWF | 0
33996 | 7068068_001001_005005_00010002_06001 | NS-Leitungstyp_fiktiv | 33342 | 22455 | 0.003 | 0 | 0 | 0 | 0 | 0.307 | 1 | 1 | cs | TRUE | 0 | 0 | 0 | 0.00403 | 80 |  | 33996 | SWF | 0

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_set_vm_pu | description | equipment
165 | 6068068_000000_000000_00000000_05001 | MSNS_0089 | 22454 | 22455 | 0.4 | 20 | 0.4 | 3.74 | 1.35 | 0.6 | 0.3 | 150 | [6 empty] | 0 | FALSE | 1 | 1 | TRUE | 3 | 0 | 100 | 0 | 0.9 | 1

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
12944 | 11.0391 | 49.713 | 11.039 | 49.713 | 11.0388 | 49.713 | 11.0388 | 49.713 | 11.0388 | 49.713 | 11.0388 | 49.713 | 11.0388 | 49.713
13193 | 11.0381 | 49.7129 | 11.0381 | 49.7129 | 11.0381 | 49.7129 | 11.0382 | 49.7129
13352 | 11.0379 | 49.7145 | 11.0379 | 49.7145 | 11.0378 | 49.7145 | 11.0378 | 49.7145 | 11.0378 | 49.7145 | 11.0377 | 49.7145 | 11.0377 | 49.7145 | 11.0377 | 49.7145 | 11.0377 | 49.7145
13353 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155
13423 | 11.0392 | 49.7129 | 11.0392 | 49.7129
13469 | 11.0393 | 49.7152 | 11.0393 | 49.7152 | 11.0393 | 49.7152 | 11.0393 | 49.7152
13559 | 11.039 | 49.7137 | 11.0391 | 49.7137 | 11.0391 | 49.7137
13599 | 11.038 | 49.7159 | 11.038 | 49.7159 | 11.0379 | 49.7159 | 11.0379 | 49.716 | 11.0379 | 49.7161 | 11.0379 | 49.7161 | 11.0377 | 49.7161 | 11.0377 | 49.7161
13662 | 11.0399 | 49.7138 | 11.0399 | 49.7139 | 11.0399 | 49.714 | 11.0399 | 49.714 | 11.0399 | 49.714 | 11.0399 | 49.714 | 11.04 | 49.7141 | 11.04 | 49.714 | 11.04 | 49.714
13752 | 11.038 | 49.7136 | 11.038 | 49.7136 | 11.0379 | 49.7136 | 11.0378 | 49.7136 | 11.0378 | 49.7136 | 11.0377 | 49.7136 | 11.0377 | 49.7136
13866 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144
13879 | 11.0399 | 49.7137 | 11.0398 | 49.7137 | 11.0398 | 49.7137 | 11.0397 | 49.7137 | 11.0397 | 49.7137 | 11.0397 | 49.7136
14007 | 11.0387 | 49.7159 | 11.0387 | 49.7159 | 11.0387 | 49.7159 | 11.0387 | 49.7159 | 11.0387 | 49.716 | 11.0387 | 49.716 | 11.0387 | 49.716
14046 | 11.0393 | 49.7152 | 11.0393 | 49.7152 | 11.0393 | 49.7152
14102 | 11.0388 | 49.7139 | 11.0388 | 49.7139 | 11.0388 | 49.7139 | 11.0387 | 49.7139 | 11.0386 | 49.7139 | 11.0386 | 49.7139 | 11.0386 | 49.7139
14139 | 11.0379 | 49.7152 | 11.0379 | 49.7152 | 11.0378 | 49.7152 | 11.0377 | 49.7152 | 11.0377 | 49.7152
14185 | 11.0389 | 49.7146 | 11.0389 | 49.7146 | 11.0389 | 49.7146 | 11.0389 | 49.7146 | 11.0388 | 49.7146 | 11.0388 | 49.7147 | 11.0388 | 49.7147
14345 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7129
14360 | 11.0379 | 49.7147 | 11.0379 | 49.7147 | 11.0379 | 49.7147 | 11.0378 | 49.7147 | 11.0378 | 49.7147 | 11.0377 | 49.7147 | 11.0377 | 49.7147 | 11.0377 | 49.7147 | 11.0377 | 49.7147
14515 | 11.038 | 49.7131 | 11.038 | 49.7131 | 11.038 | 49.7131 | 11.0379 | 49.7131 | 11.0379 | 49.7132 | 11.0379 | 49.7132 | 11.0378 | 49.7132 | 11.0378 | 49.7132 | 11.0378 | 49.7132 | 11.0378 | 49.7132 | 11.0378 | 49.7132 | 11.0378 | 49.7132
14591 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7131 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7133 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.0389 | 49.7138 | 11.0389 | 49.7138
14732 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.0391 | 49.7152
14759 | 11.0383 | 49.7142 | 11.0383 | 49.7142 | 11.0383 | 49.7142 | 11.0383 | 49.7142 | 11.0383 | 49.7142 | 11.0383 | 49.7142 | 11.0383 | 49.7143 | 11.0383 | 49.7143 | 11.0382 | 49.7143 | 11.0382 | 49.7143 | 11.0382 | 49.7143 | 11.0382 | 49.7143
14790 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.0391 | 49.7142 | 11.0391 | 49.7142 | 11.0391 | 49.7141
14956 | 11.0386 | 49.7142 | 11.0386 | 49.7142 | 11.0386 | 49.7141 | 11.0386 | 49.7141 | 11.0387 | 49.7141 | 11.0387 | 49.7141
15026 | 11.0402 | 49.7134 | 11.04 | 49.7134 | 11.04 | 49.7134
15064 | 11.0381 | 49.7128 | 11.038 | 49.7128 | 11.038 | 49.7129 | 11.038 | 49.7129 | 11.038 | 49.7129 | 11.0379 | 49.7129 | 11.0379 | 49.7129 | 11.0378 | 49.7129 | 11.0377 | 49.7129 | 11.0377 | 49.7129 | 11.0377 | 49.7129
15107 | 11.0389 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137
15156 | 11.0383 | 49.7159 | 11.0383 | 49.7158 | 11.0383 | 49.7158 | 11.0383 | 49.7158
15235 | 11.0391 | 49.7152 | 11.0391 | 49.7152 | 11.039 | 49.7152 | 11.0389 | 49.7152 | 11.0389 | 49.7152
15240 | 11.0391 | 49.7132 | 11.0392 | 49.7132 | 11.0392 | 49.7132
15305 | 11.0381 | 49.7127 | 11.0381 | 49.7127 | 11.038 | 49.7127 | 11.038 | 49.7127 | 11.0378 | 49.7127 | 11.0378 | 49.7127 | 11.0378 | 49.7127
15323 | 11.0377 | 49.7143 | 11.0377 | 49.7143 | 11.0377 | 49.7143 | 11.0377 | 49.7142 | 11.0377 | 49.7142 | 11.0378 | 49.7142 | 11.0378 | 49.7142 | 11.0378 | 49.7141 | 11.0378 | 49.7141 | 11.0378 | 49.7141 | 11.0377 | 49.7141 | 11.0377 | 49.7141 | 11.0377 | 49.7141 | 11.0377 | 49.714 | 11.0377 | 49.714 | 11.0377 | 49.714
15341 | 11.0379 | 49.715 | 11.0379 | 49.715 | 11.0379 | 49.715 | 11.0378 | 49.715 | 11.0377 | 49.715 | 11.0377 | 49.715
15349 | 11.0391 | 49.713 | 11.0391 | 49.713 | 11.0391 | 49.713 | 11.0391 | 49.713 | 11.0391 | 49.713
15350 | 11.0385 | 49.7142 | 11.0385 | 49.7143 | 11.0385 | 49.7143 | 11.0385 | 49.7143 | 11.0385 | 49.7143 | 11.0385 | 49.7143
15433 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.0391 | 49.7151 | 11.039 | 49.7151 | 11.0389 | 49.7151 | 11.0389 | 49.7151 | 11.0389 | 49.7151 | 11.0389 | 49.7151 | 11.0388 | 49.7151 | 11.0388 | 49.7151 | 11.0388 | 49.7151 | 11.0388 | 49.7151 | 11.0387 | 49.7151 | 11.0387 | 49.7151 | 11.0387 | 49.7151
15729 | 11.0379 | 49.7139 | 11.038 | 49.7139 | 11.038 | 49.7139
16000 | 11.039 | 49.7135 | 11.0391 | 49.7135 | 11.0391 | 49.7135
16084 | 11.0379 | 49.7156 | 11.038 | 49.7156 | 11.0381 | 49.7156 | 11.0381 | 49.7156 | 11.0382 | 49.7156
16286 | 11.0383 | 49.7159 | 11.0383 | 49.7159 | 11.0383 | 49.7159 | 11.0383 | 49.7159 | 11.0384 | 49.7159 | 11.0384 | 49.716 | 11.0384 | 49.716
16308 | 11.038 | 49.7131 | 11.0381 | 49.7131 | 11.0382 | 49.7131
16309 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0393 | 49.7129 | 11.0394 | 49.713 | 11.0394 | 49.713 | 11.0394 | 49.713
17295 | 11.0379 | 49.715 | 11.0379 | 49.715 | 11.0379 | 49.715 | 11.0381 | 49.715 | 11.0381 | 49.715 | 11.0381 | 49.715
17377 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0388 | 49.7144 | 11.0388 | 49.7144 | 11.0387 | 49.7145 | 11.0387 | 49.7145 | 11.0387 | 49.7145
17456 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0403 | 49.7131 | 11.0403 | 49.7131 | 11.0403 | 49.7131 | 11.0403 | 49.7131 | 11.0403 | 49.7131 | 11.0403 | 49.7131 | 11.0403 | 49.7131
17572 | 11.0382 | 49.7142 | 11.0382 | 49.7142 | 11.0382 | 49.7141 | 11.0382 | 49.7141 | 11.0381 | 49.7141 | 11.0382 | 49.7141 | 11.0382 | 49.7141
17608 | 11.0382 | 49.7126 | 11.0382 | 49.7126 | 11.0382 | 49.7126 | 11.0382 | 49.7126 | 11.0382 | 49.7125 | 11.0382 | 49.7125 | 11.0382 | 49.7125 | 11.038 | 49.7125 | 11.0379 | 49.7124 | 11.0379 | 49.7124 | 11.0379 | 49.7124 | 11.0378 | 49.7124 | 11.0378 | 49.7124 | 11.0378 | 49.7124 | 11.0378 | 49.7124
17686 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137 | 11.039 | 49.7137
17728 | 11.0389 | 49.7127 | 11.0389 | 49.7126 | 11.0387 | 49.7126 | 11.0386 | 49.7125 | 11.0386 | 49.7125 | 11.0386 | 49.7125
17952 | 11.0396 | 49.714 | 11.0395 | 49.714 | 11.0395 | 49.714 | 11.0395 | 49.714
17993 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.039 | 49.7138
18048 | 11.0379 | 49.7154 | 11.038 | 49.7155 | 11.038 | 49.7155 | 11.0381 | 49.7155 | 11.0381 | 49.7155
18206 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157
18313 | 11.0392 | 49.7159 | 11.0393 | 49.7159 | 11.0393 | 49.7159 | 11.0393 | 49.7159
18343 | 11.039 | 49.7148 | 11.039 | 49.7148 | 11.039 | 49.7148 | 11.039 | 49.7148 | 11.039 | 49.7148 | 11.039 | 49.7148 | 11.039 | 49.7148 | 11.039 | 49.7148 | 11.0391 | 49.7148 | 11.0391 | 49.7148
18378 | 11.0382 | 49.7159 | 11.0382 | 49.7159 | 11.0382 | 49.7158 | 11.0382 | 49.7158 | 11.0382 | 49.7158
18409 | 11.0379 | 49.7154 | 11.0379 | 49.7154 | 11.0378 | 49.7154 | 11.0377 | 49.7154 | 11.0377 | 49.7154
18540 | 11.039 | 49.7132 | 11.039 | 49.7132 | 11.039 | 49.7132 | 11.0388 | 49.7132 | 11.0387 | 49.7132 | 11.0387 | 49.7132 | 11.0387 | 49.7132
18654 | 11.0389 | 49.7145 | 11.0389 | 49.7145 | 11.039 | 49.7145 | 11.0391 | 49.7145 | 11.0391 | 49.7145 | 11.0391 | 49.7145 | 11.0391 | 49.7145
18695 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0394 | 49.7164
18775 | 11.0379 | 49.7152 | 11.0379 | 49.7152 | 11.0381 | 49.7152 | 11.0381 | 49.7152
18796 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132
18891 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.0379 | 49.7158 | 11.0379 | 49.7158 | 11.0379 | 49.7158 | 11.0378 | 49.7158 | 11.0378 | 49.7158
18925 | 11.038 | 49.7138 | 11.0379 | 49.7138 | 11.0379 | 49.7138 | 11.0379 | 49.7138 | 11.0379 | 49.7138 | 11.0379 | 49.7138 | 11.0378 | 49.7138 | 11.0378 | 49.7138 | 11.0378 | 49.7138 | 11.0377 | 49.7138 | 11.0377 | 49.7138 | 11.0377 | 49.7138 | 11.0377 | 49.7138
19091 | 11.0379 | 49.7149 | 11.0379 | 49.7149 | 11.0378 | 49.7149 | 11.0378 | 49.7149 | 11.0378 | 49.7149 | 11.0377 | 49.7149 | 11.0377 | 49.7149 | 11.0376 | 49.7149 | 11.0376 | 49.7149 | 11.0376 | 49.7149 | 11.0376 | 49.7149 | 11.0376 | 49.7149 | 11.0376 | 49.7149
19400 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7139 | 11.0389 | 49.7139 | 11.0388 | 49.7139 | 11.0388 | 49.7139 | 11.0388 | 49.7139
19464 | 11.0389 | 49.7159 | 11.0389 | 49.7159 | 11.039 | 49.7159 | 11.039 | 49.7159 | 11.039 | 49.7159 | 11.039 | 49.716 | 11.039 | 49.716
19632 | 11.0379 | 49.7148 | 11.038 | 49.7148 | 11.0381 | 49.7148
19654 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135
19655 | 11.039 | 49.7149 | 11.039 | 49.7149 | 11.0389 | 49.7149 | 11.0388 | 49.7149 | 11.0388 | 49.7149
19709 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0391 | 49.7155 | 11.0391 | 49.7155 | 11.039 | 49.7155
20027 | 11.0394 | 49.7128 | 11.0394 | 49.7128 | 11.0394 | 49.7128 | 11.0394 | 49.7129 | 11.0394 | 49.7129 | 11.0394 | 49.7129 | 11.0394 | 49.7129 | 11.0395 | 49.7129 | 11.0395 | 49.7129
20102 | 11.0379 | 49.7156 | 11.0379 | 49.7156 | 11.0379 | 49.7156 | 11.0379 | 49.7156 | 11.0379 | 49.7156 | 11.0379 | 49.7156 | 11.0377 | 49.7156 | 11.0377 | 49.7156 | 11.0377 | 49.7156 | 11.0377 | 49.7156
20211 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7138
20310 | 11.038 | 49.7157 | 11.0379 | 49.7157 | 11.0379 | 49.7157 | 11.0377 | 49.7157 | 11.0377 | 49.7157 | 11.0377 | 49.7157
20373 | 11.0392 | 49.7161 | 11.0392 | 49.7161 | 11.0392 | 49.7161 | 11.0392 | 49.7161 | 11.0392 | 49.7161 | 11.0392 | 49.7161
20383 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7155
20456 | 11.038 | 49.7135 | 11.0381 | 49.7135 | 11.0381 | 49.7135
20457 | 11.0381 | 49.7159 | 11.0381 | 49.7159 | 11.0381 | 49.716 | 11.0381 | 49.716
20489 | 11.0392 | 49.7155 | 11.0393 | 49.7155 | 11.0393 | 49.7155
20546 | 11.039 | 49.7149 | 11.039 | 49.7149 | 11.039 | 49.7149 | 11.039 | 49.7149 | 11.039 | 49.7149 | 11.039 | 49.7149 | 11.039 | 49.7149 | 11.039 | 49.7149
20574 | 11.0397 | 49.7139 | 11.0396 | 49.7139 | 11.0396 | 49.7139
20641 | 11.0386 | 49.7159 | 11.0386 | 49.7158 | 11.0386 | 49.7158
20678 | 11.0401 | 49.7139 | 11.0402 | 49.7139 | 11.0402 | 49.7139 | 11.0403 | 49.7139 | 11.0403 | 49.7139 | 11.0402 | 49.714 | 11.0403 | 49.714 | 11.0403 | 49.714
20975 | 11.0392 | 49.7161 | 11.0392 | 49.7161 | 11.0393 | 49.7161 | 11.0393 | 49.7161 | 11.0393 | 49.7161
20991 | 11.0389 | 49.7127 | 11.0389 | 49.7128 | 11.0389 | 49.7128 | 11.0388 | 49.7128 | 11.0388 | 49.7128 | 11.0388 | 49.7128
21052 | 11.0393 | 49.7165 | 11.0393 | 49.7165 | 11.0393 | 49.7165 | 11.0393 | 49.7165 | 11.0393 | 49.7165 | 11.0393 | 49.7165 | 11.0393 | 49.7165 | 11.0393 | 49.7165 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164 | 11.0393 | 49.7164
21076 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.039 | 49.7135 | 11.0389 | 49.7134 | 11.0388 | 49.7134 | 11.0387 | 49.7134
21110 | 11.0389 | 49.7137 | 11.0388 | 49.7137 | 11.0387 | 49.7137 | 11.0387 | 49.7137 | 11.0387 | 49.7137
21619 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7159
21907 | 11.0392 | 49.7157 | 11.0393 | 49.7157 | 11.0393 | 49.7157
22043 | 11.0401 | 49.7139 | 11.0401 | 49.7138 | 11.0401 | 49.7138 | 11.0401 | 49.7137 | 11.0402 | 49.7137 | 11.0402 | 49.7137
22169 | 11.0377 | 49.7143 | 11.0377 | 49.7143 | 11.0377 | 49.7143
22322 | 11.0381 | 49.7126 | 11.0381 | 49.7126 | 11.038 | 49.7125 | 11.038 | 49.7125 | 11.038 | 49.7125 | 11.0379 | 49.7125 | 11.0379 | 49.7125 | 11.0378 | 49.7125 | 11.0377 | 49.7125 | 11.0377 | 49.7125 | 11.0377 | 49.7125
22411 | 11.0383 | 49.7126 | 11.0383 | 49.7126 | 11.0383 | 49.7126 | 11.0383 | 49.7126 | 11.0383 | 49.7126
22460 | 11.0379 | 49.7146 | 11.0381 | 49.7146 | 11.0381 | 49.7146 | 11.0381 | 49.7146
22569 | 11.0379 | 49.7144 | 11.038 | 49.7144 | 11.038 | 49.7144
22619 | 11.0389 | 49.7159 | 11.0389 | 49.7158 | 11.0389 | 49.7158 | 11.0389 | 49.7158 | 11.0389 | 49.7158
22714 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.0391 | 49.7132 | 11.039 | 49.7132
22830 | 11.0396 | 49.714 | 11.0397 | 49.7139 | 11.0397 | 49.7139
22831 | 11.0397 | 49.7139 | 11.0398 | 49.7138
23924 | 11.0389 | 49.7138 | 11.0389 | 49.7138 | 11.0389 | 49.7139 | 11.0389 | 49.7139 | 11.0389 | 49.714 | 11.0389 | 49.7141 | 11.0389 | 49.7141 | 11.0389 | 49.7141 | 11.0389 | 49.7142 | 11.0389 | 49.7142 | 11.0389 | 49.7142 | 11.0389 | 49.7142 | 11.0389 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.0391 | 49.7142 | 11.0393 | 49.7143 | 11.0393 | 49.7143 | 11.0393 | 49.7143 | 11.0393 | 49.7143
24217 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142
24218 | 11.039 | 49.7142 | 11.0391 | 49.7143 | 11.0393 | 49.7143 | 11.0393 | 49.7143
24230 | 11.0392 | 49.7128 | 11.0391 | 49.7128 | 11.0391 | 49.7128
26673 | 11.0391 | 49.7152 | 11.0393 | 49.7152
28035 | 11.0393 | 49.7143 | 11.0393 | 49.7143 | 11.0393 | 49.7143 | 11.0391 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7144 | 11.0389 | 49.7144 | 11.0389 | 49.7144
28036 | 11.0389 | 49.7144 | 11.0389 | 49.7145 | 11.0389 | 49.7145
28037 | 11.0389 | 49.7145 | 11.0389 | 49.7146 | 11.0389 | 49.7146
28038 | 11.0389 | 49.7146 | 11.039 | 49.7148 | 11.039 | 49.7148
28039 | 11.039 | 49.7148 | 11.039 | 49.7149 | 11.039 | 49.7149
28040 | 11.039 | 49.7149 | 11.0391 | 49.715 | 11.0391 | 49.7151
28041 | 11.0391 | 49.7151 | 11.0391 | 49.7152 | 11.0391 | 49.7152
28042 | 11.0391 | 49.7152
28043 | 11.0391 | 49.7152 | 11.0392 | 49.7155 | 11.0392 | 49.7155
28044 | 11.0392 | 49.7155
28045 | 11.0392 | 49.7155 | 11.0392 | 49.7155 | 11.0392 | 49.7156 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7157
28046 | 11.0392 | 49.7157 | 11.0392 | 49.7157 | 11.0392 | 49.7158 | 11.0392 | 49.7159 | 11.0392 | 49.7159
28047 | 11.0392 | 49.7159 | 11.0392 | 49.7159 | 11.0392 | 49.7161 | 11.0392 | 49.7161 | 11.0392 | 49.7161
28048 | 11.0392 | 49.7161 | 11.0392 | 49.7161 | 11.0392 | 49.7163 | 11.0393 | 49.7164 | 11.0393 | 49.7165
28082 | 11.0398 | 49.7138 | 11.0399 | 49.7138
28083 | 11.0399 | 49.7138 | 11.04 | 49.7139 | 11.0401 | 49.7139
28905 | 11.039 | 49.7159 | 11.0389 | 49.7159
28906 | 11.0389 | 49.7159
28907 | 11.0389 | 49.7159 | 11.0388 | 49.7159 | 11.0387 | 49.7159 | 11.0387 | 49.7159
28908 | 11.0387 | 49.7159 | 11.0387 | 49.7159 | 11.0386 | 49.7159
28909 | 11.0386 | 49.7159 | 11.0384 | 49.7159 | 11.0383 | 49.7159
28910 | 11.0383 | 49.7159
28911 | 11.0383 | 49.7159 | 11.0382 | 49.7159 | 11.0382 | 49.7159
28912 | 11.0382 | 49.7159
28956 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7128 | 11.0391 | 49.7128 | 11.0392 | 49.7127 | 11.0392 | 49.7127 | 11.0391 | 49.7127 | 11.039 | 49.7127 | 11.0389 | 49.7127
28957 | 11.0389 | 49.7127
28958 | 11.0389 | 49.7127 | 11.0386 | 49.7126 | 11.0383 | 49.7126
28959 | 11.0383 | 49.7126 | 11.0382 | 49.7126 | 11.0382 | 49.7126
28960 | 11.0382 | 49.7126 | 11.0381 | 49.7126 | 11.0381 | 49.7126
28961 | 11.0381 | 49.7126 | 11.0381 | 49.7126 | 11.0381 | 49.7126 | 11.0381 | 49.7127 | 11.0381 | 49.7127
28962 | 11.0381 | 49.7127 | 11.0381 | 49.7127 | 11.0381 | 49.7128 | 11.0381 | 49.7128 | 11.0381 | 49.7128
28963 | 11.0381 | 49.7128 | 11.0381 | 49.7129
28964 | 11.0381 | 49.7129 | 11.038 | 49.7129 | 11.038 | 49.7131
28965 | 11.038 | 49.7131
28966 | 11.038 | 49.7131 | 11.038 | 49.7133 | 11.038 | 49.7134 | 11.038 | 49.7135
28967 | 11.038 | 49.7135 | 11.038 | 49.7136
28968 | 11.038 | 49.7136 | 11.038 | 49.7137 | 11.038 | 49.7138
28969 | 11.038 | 49.7138 | 11.0379 | 49.7138 | 11.0379 | 49.7139
28970 | 11.0379 | 49.7139 | 11.0379 | 49.714 | 11.0379 | 49.714 | 11.0379 | 49.7141
29366 | 11.0381 | 49.7159 | 11.0382 | 49.7159
29484 | 11.0398 | 49.7138 | 11.0399 | 49.7137
29485 | 11.0399 | 49.7137 | 11.04 | 49.7136 | 11.04 | 49.7136 | 11.0401 | 49.7135 | 11.0401 | 49.7135 | 11.0402 | 49.7134
29486 | 11.0402 | 49.7134 | 11.0402 | 49.7133 | 11.0403 | 49.7132 | 11.0403 | 49.7132 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713
29708 | 11.0378 | 49.7141 | 11.0378 | 49.7142 | 11.0377 | 49.7142 | 11.0377 | 49.7142 | 11.0377 | 49.7142 | 11.0377 | 49.7143 | 11.0377 | 49.7143 | 11.0377 | 49.7143
30005 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7129 | 11.0391 | 49.7129
30006 | 11.0391 | 49.7129 | 11.0391 | 49.713 | 11.0391 | 49.713
30007 | 11.0391 | 49.713 | 11.0391 | 49.7131 | 11.0391 | 49.7132
30008 | 11.0391 | 49.7132
30009 | 11.0391 | 49.7132 | 11.039 | 49.7133 | 11.039 | 49.7134 | 11.039 | 49.7135
30010 | 11.039 | 49.7135
30011 | 11.039 | 49.7135 | 11.039 | 49.7137 | 11.039 | 49.7137
30012 | 11.039 | 49.7137
30013 | 11.039 | 49.7137 | 11.0389 | 49.7138 | 11.0389 | 49.7138
30014 | 11.0389 | 49.7138
30315 | 11.038 | 49.7142 | 11.038 | 49.7142 | 11.038 | 49.7142 | 11.0381 | 49.7142 | 11.0382 | 49.7142
30316 | 11.0382 | 49.7142 | 11.0383 | 49.7142
30317 | 11.0383 | 49.7142 | 11.0385 | 49.7142
30318 | 11.0385 | 49.7142 | 11.0386 | 49.7142
30319 | 11.0386 | 49.7142 | 11.0387 | 49.7142 | 11.0387 | 49.7142 | 11.0387 | 49.7142 | 11.0387 | 49.7142 | 11.0388 | 49.7142 | 11.0388 | 49.7142 | 11.0388 | 49.7142 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.0389 | 49.7143 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.039 | 49.7142 | 11.0391 | 49.7142 | 11.0393 | 49.7143 | 11.0393 | 49.7143 | 11.0393 | 49.7143
30894 | 11.0381 | 49.7159 | 11.0381 | 49.7159
30895 | 11.0381 | 49.7159 | 11.038 | 49.7159 | 11.038 | 49.7159 | 11.038 | 49.7159 | 11.038 | 49.7159 | 11.038 | 49.7159 | 11.038 | 49.7159 | 11.038 | 49.7159 | 11.038 | 49.7159
30896 | 11.038 | 49.7159 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158
30897 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7158 | 11.038 | 49.7157 | 11.038 | 49.7157
30898 | 11.038 | 49.7157 | 11.0379 | 49.7156 | 11.0379 | 49.7156
30899 | 11.0379 | 49.7156
30900 | 11.0379 | 49.7156 | 11.0379 | 49.7155 | 11.0379 | 49.7154
30901 | 11.0379 | 49.7154
30902 | 11.0379 | 49.7154 | 11.0379 | 49.7153 | 11.0379 | 49.7152
30903 | 11.0379 | 49.7152
30904 | 11.0379 | 49.7152 | 11.0379 | 49.7151 | 11.0379 | 49.715
30905 | 11.0379 | 49.715
30906 | 11.0379 | 49.715 | 11.0379 | 49.7149
30907 | 11.0379 | 49.7149 | 11.0379 | 49.7148
30908 | 11.0379 | 49.7148 | 11.0379 | 49.7147 | 11.0379 | 49.7147
30909 | 11.0379 | 49.7147 | 11.0379 | 49.7146
30910 | 11.0379 | 49.7146 | 11.0379 | 49.7145 | 11.0379 | 49.7145
30911 | 11.0379 | 49.7145 | 11.0379 | 49.7144
30912 | 11.0379 | 49.7144 | 11.0379 | 49.7143 | 11.0379 | 49.7143 | 11.0379 | 49.7142 | 11.0379 | 49.7142 | 11.0379 | 49.7142 | 11.0379 | 49.7142 | 11.038 | 49.7142 | 11.038 | 49.7142 | 11.038 | 49.7142
31375 | 11.038 | 49.7142 | 11.0378 | 49.7142 | 11.0378 | 49.7141
31376 | 11.0378 | 49.7141 | 11.0377 | 49.7141 | 11.0376 | 49.7141 | 11.0376 | 49.7141 | 11.0375 | 49.7141 | 11.0375 | 49.7141 | 11.0375 | 49.7141 | 11.0374 | 49.7141 | 11.0374 | 49.7141 | 11.0374 | 49.7141 | 11.0374 | 49.7141
32300 | 11.0391 | 49.7128 | 11.0392 | 49.7128 | 11.0392 | 49.7127 | 11.0392 | 49.7127 | 11.0394 | 49.7128
32301 | 11.0394 | 49.7128 | 11.0398 | 49.7128 | 11.04 | 49.7129 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713 | 11.0404 | 49.713
33066 | 11.0392 | 49.7129 | 11.0392 | 49.7129
33126 | 11.0391 | 49.7129 | 11.0392 | 49.7129
33650 | 11.0392 | 49.7128 | 11.0392 | 49.7129
33921 | 11.0391 | 49.7129 | 11.0392 | 49.7129
33996 | 11.0391 | 49.7129 | 11.0392 | 49.7129

## bus_geodata
| x | y | coords
15873 | 11.0388 | 49.7149
20997 | 11.0393 | 49.7152
29701 | 11.0386 | 49.7159
33286 | 11.0378 | 49.7141
28680 | 11.0389 | 49.7159
15884 | 11.0387 | 49.7151
15888 | 11.0389 | 49.7152
24593 | 11.0386 | 49.7142
19994 | 11.0391 | 49.7145
27169 | 11.0389 | 49.7127
31269 | 11.0379 | 49.7144
29734 | 11.0401 | 49.7139
16423 | 11.0377 | 49.7157
20008 | 11.0391 | 49.7135
20521 | 11.0387 | 49.7141
28205 | 11.038 | 49.7158
23093 | 11.0392 | 49.7129
29239 | 11.0379 | 49.7156
13368 | 11.0377 | 49.7154
18493 | 11.0388 | 49.7128
27709 | 11.0392 | 49.7159
33342 | 11.0391 | 49.7129
19522 | 11.0378 | 49.7124
28230 | 11.038 | 49.7138
25671 | 11.0379 | 49.7156
31305 | 11.0389 | 49.7159
21071 | 11.039 | 49.7155
15953 | 11.0377 | 49.715
20561 | 11.0386 | 49.7158
24658 | 11.0402 | 49.7134
27738 | 11.039 | 49.7148
22621 | 11.0391 | 49.713
19040 | 11.038 | 49.7139
23140 | 11.0393 | 49.7152
31845 | 11.0389 | 49.7138
20074 | 11.039 | 49.7138
33388 | 11.038 | 49.7142
24173 | 11.038 | 49.7131
14447 | 11.0383 | 49.7158
27767 | 11.0382 | 49.7159
18552 | 11.0394 | 49.713
24696 | 11.0381 | 49.7128
23675 | 11.0387 | 49.7159
31372 | 11.0391 | 49.7132
27793 | 11.0379 | 49.7154
17042 | 11.0385 | 49.7143
29332 | 11.0389 | 49.7138
19100 | 11.0397 | 49.7136
19101 | 11.0392 | 49.7132
26780 | 11.0379 | 49.715
28832 | 11.0379 | 49.7148
24742 | 11.0389 | 49.7137
24743 | 11.039 | 49.7137
20136 | 11.0381 | 49.7135
21166 | 11.0387 | 49.7134
28850 | 11.039 | 49.7135
28851 | 11.039 | 49.7149
24246 | 11.0391 | 49.7129
24247 | 11.0389 | 49.7138
21688 | 11.0404 | 49.713
16058 | 11.0377 | 49.7138
31418 | 11.0398 | 49.7138
23229 | 11.039 | 49.7137
13509 | 11.04 | 49.7134
19147 | 11.0387 | 49.7132
28365 | 11.0379 | 49.7149
31950 | 11.039 | 49.7142
31952 | 11.0392 | 49.7128
31953 | 11.0391 | 49.7128
24786 | 11.0383 | 49.7159
19156 | 11.0388 | 49.713
23774 | 11.0388 | 49.7139
15583 | 11.0382 | 49.7129
14561 | 11.0381 | 49.715
28898 | 11.0392 | 49.7155
17124 | 11.0389 | 49.7158
16101 | 11.0393 | 49.7157
19686 | 11.0383 | 49.7126
23269 | 11.038 | 49.7159
29414 | 11.038 | 49.7157
17130 | 11.0391 | 49.7141
18160 | 11.0377 | 49.7161
33520 | 11.0374 | 49.7141
20723 | 11.0396 | 49.7139
25331 | 11.0379 | 49.7139
27379 | 11.0396 | 49.714
15617 | 11.0381 | 49.7155
14594 | 11.0382 | 49.7158
21249 | 11.0377 | 49.7136
16644 | 11.0395 | 49.7129
23810 | 11.0379 | 49.7152
27906 | 11.039 | 49.7132
19210 | 11.0391 | 49.7137
25867 | 11.0383 | 49.7159
19216 | 11.0402 | 49.7137
29465 | 11.0392 | 49.7161
21274 | 11.0378 | 49.7158
29466 | 11.0392 | 49.7161
25886 | 11.038 | 49.7131
18209 | 11.0382 | 49.7143
20770 | 11.0377 | 49.7156
24866 | 11.0391 | 49.7132
29476 | 11.0392 | 49.7155
23333 | 11.0399 | 49.7138
14119 | 11.04 | 49.714
21292 | 11.0377 | 49.7147
14125 | 11.0377 | 49.7145
23853 | 11.0389 | 49.7146
29999 | 11.0389 | 49.7127
19761 | 11.0381 | 49.7152
30513 | 11.0392 | 49.7159
19255 | 11.0377 | 49.7152
17208 | 11.0393 | 49.7155
19767 | 11.0382 | 49.7141
24384 | 11.0391 | 49.7152
14145 | 11.0377 | 49.7125
20289 | 11.0377 | 49.7129
24385 | 11.0391 | 49.7152
33090 | 11.039 | 49.7159
27461 | 11.0379 | 49.7154
13127 | 11.0387 | 49.7137
17736 | 11.0394 | 49.7164
17231 | 11.0384 | 49.716
19279 | 11.0403 | 49.7131
19791 | 11.0387 | 49.716
22864 | 11.0381 | 49.7129
31058 | 11.0381 | 49.7126
24919 | 11.0381 | 49.7127
19288 | 11.0387 | 49.7145
16217 | 11.0388 | 49.7147
24409 | 11.0383 | 49.7142
30041 | 11.0393 | 49.7165
13662 | 11.0376 | 49.7149
17759 | 11.0393 | 49.7152
13668 | 11.0395 | 49.714
29540 | 11.038 | 49.7135
29541 | 11.0381 | 49.7159
28011 | 11.0389 | 49.7145
24940 | 11.0377 | 49.7143
29177 | 11.0394 | 49.7128
30063 | 11.039 | 49.7135
13172 | 11.0382 | 49.7156
33142 | 11.0382 | 49.7159
15737 | 11.0393 | 49.7161
24441 | 11.039 | 49.7142
33148 | 11.0391 | 49.7129
16765 | 11.0381 | 49.716
23421 | 11.038 | 49.7136
24958 | 11.0379 | 49.715
33149 | 11.0379 | 49.7141
20868 | 11.0381 | 49.7146
24965 | 11.0391 | 49.713
24966 | 11.0385 | 49.7142
19849 | 11.0393 | 49.7159
28045 | 11.0393 | 49.7164
27031 | 11.0382 | 49.7142
32664 | 11.0391 | 49.7152
31130 | 11.0383 | 49.7126
15784 | 11.0377 | 49.714
29618 | 11.039 | 49.7149
22454 | 11.0392 | 49.7129
22455 | 11.0392 | 49.7129
27063 | 11.0382 | 49.7126
15293 | 11.0391 | 49.7148
13757 | 11.0386 | 49.7139
16829 | 11.0377 | 49.7143
31166 | 11.0379 | 49.7146
21443 | 11.0382 | 49.7131
20420 | 11.038 | 49.7144
33220 | 11.0381 | 49.7159
24006 | 11.0391 | 49.7129
24007 | 11.0391 | 49.7129
29641 | 11.0397 | 49.7139
21962 | 11.0393 | 49.7143
28114 | 11.0379 | 49.7152
25044 | 11.0391 | 49.7151
28628 | 11.0389 | 49.7138
19414 | 11.0381 | 49.7148
24023 | 11.0379 | 49.7147
13273 | 11.0386 | 49.7125
27613 | 11.0392 | 49.7157
27614 | 11.0392 | 49.7157
19423 | 11.0392 | 49.7129
13798 | 11.0378 | 49.7132
28134 | 11.0391 | 49.7132
20968 | 11.0403 | 49.714
23529 | 11.0389 | 49.7144
23530 | 11.0389 | 49.7144
15855 | 11.039 | 49.716
14321 | 11.0378 | 49.7127
23025 | 11.0379 | 49.7145
23026 | 11.0392 | 49.7155
23027 | 11.0392 | 49.7155
25587 | 11.039 | 49.7135
23545 | 11.0399 | 49.7137
27134 | 11.039 | 49.7137

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | endtemp_degree | r0_ohm_per_km | x0_ohm_per_km | c0_nf_per_km
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
NS-Leitungstypen\15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYM 4x1.5 | 0 | 12.1187 | 0.10776 | 0.025 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.43103 | 0
NYCWY 3x70/35 | 1120 | 0.26995 | 0.07477 | 0.227 | cs | 0 | 0.00393 | 160 | 1.0798 | 0.29908 | 672
NAYCWY 3x50/50 | 980 | 0.6417 | 0.077597 | 0.142 | cs | 0 | 0.00403 | 160 | 2.5668 | 0.31039 | 588
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
NAYBY 4x70sm 0.6/1kV | 810 | 0.4442 | 0.075398 | 0.175 | cs | 70 | 0.00403 | 160 | 1.7767 | 0.30159 | 367.6
NAYY 4x95SE 0.6/1kV | 770 | 0.3208 | 0.081996 | 0.211 | cs | 95 | 0.00403 | 160 | 1.2833 | 0.32798 | 349.2
NAYCWY 3x35/16 | 960 | 0.86558 | 0.078854 | 0.123 | cs | 0 | 0.00403 | 160 | 3.4623 | 0.31542 | 576
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NYCWY 3x25/25 | 840 | 0.72796 | 0.080739 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9118 | 0.32296 | 504
NYY-J 3x240SM 0.6/1kV | 1390 | 0.0777 | 0.072571 | 0.56 | cs | 240 | 0.00393 | 160 | 0.3106 | 0.29028 | 643.2
NKBA 4x95sm 0.6/1kV | 1000 | 0.1953 | 0.065973 | 0.28 | cs | 95 | 0.00393 | 180 | 0.7812 | 0.26389 | 514.6
NAYY 4x185SE 0.6/1kV | 830 | 0.165 | 0.080425 | 0.307 | cs | 185 | 0.00403 | 160 | 0.66 | 0.3217 | 385.9
NYY 4x10 | 0 | 1.8303 | 0.094562 | 0.075 | cs | 0 | 0.00393 | 160 | 7.3214 | 0.37825 | 0
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A_air | 12.6 | 0.413 | 0.29 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYY-J 4x16 | 0 | 1.1534 | 0.089535 | 0.098 | cs | 0 | 0.00393 | 160 | 4.6135 | 0.35814 | 0
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
NA2XS(F)2Y 1x150RM 12/20kV ir | 254 | 0.227 | 0.19541 | 0.353 | cs | 150 | 0.00403 | 250 | 0.832 | 0.309 | 253.6
NYY-O 3x120SM 0.6/1kV | 1309.9999 | 0.154 | 0.073199 | 0.309 | cs | 120 | 0.00393 | 160 | 0.6159 | 0.2928 | 569.7
NAYBY 4x150sm 0.6/1kV | 910 | 0.2075 | 0.072257 | 0.27 | cs | 150 | 0.00403 | 160 | 0.83 | 0.28903 | 441.1
NYY-J 4x25 | 0 | 0.72712 | 0.087965 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9085 | 0.35186 | 0
NYCWY 3x16/16 | 800 | 1.1534 | 0.08231 | 0.099 | cs | 0 | 0.00393 | 160 | 4.6135 | 0.32924 | 480
NYCWY 3x35/35 | 960 | 0.52486 | 0.077912 | 0.156 | cs | 0 | 0.00393 | 160 | 2.0995 | 0.31165 | 576
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NAYY 4x70SE 0.6/1kV | 750 | 0.4442 | 0.08231 | 0.176 | cs | 70 | 0.00403 | 160 | 1.7767 | 0.32924 | 312.4
NYY-O 3x70SM 0.6/1kV | 1130 | 0.2686 | 0.07477 | 0.225 | cs | 70 | 0.00393 | 160 | 1.0745 | 0.29908 | 477.8
NA2XS(F)2Y 1x240RM 12/20kV ir | 304 | 0.144 | 0.18253 | 0.456 | cs | 240 | 0.00403 | 250 | 0.749 | 0.303 | 303.2
NA2XS2Y 1x240RM 12/20kV ir | 304 | 0.144 | 0.18253 | 0.456 | cs | 240 | 0.00403 | 250 | 0.749 | 0.303 | 303.2
NEKBA 3x70rm 12/20kV | 280 | 0.2705 | 0.11624 | 0.22 | cs | 70 | 0.00393 | 155 | 1.0821 | 0.46496 | 284.9
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
15-AL1/3-ST1A 0.4_air | 11 | 1.8769 | 0.35 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
NAEKBA 3x95rm 12/20kV | 310 | 0.3203 | 0.10996 | 0.21 | cs | 95 | 0.00403 | 155 | 1.2814 | 0.43982 | 314.3
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
NYCWY 3x95/95 | 1160 | 0.19473 | 0.07477 | 0.272 | cs | 0 | 0.00393 | 160 | 0.77894 | 0.29908 | 696
NYY-J 3x70SM 0.6/1kV | 1130 | 0.2686 | 0.07477 | 0.276 | cs | 70 | 0.00393 | 160 | 1.0745 | 0.29908 | 477.8
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
N2XS(F)2Y 1x300RM/25 12/20kV it | 329 | 0.065 | 0.10996 | 0.597 | cs | 300 | 0.00393 | 250 | 0.2599 | 0.43982 | 328
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
NA2XS(F)2Y 1x95RM 12/20kV ir | 216 | 0.334 | 0.20986 | 0.282 | cs | 95 | 0.00403 | 250 | 1.134 | 0.563 | 215
NA2XS2Y 1x120RM 12/20kV ir | 235 | 0.267 | 0.20326 | 0.32 | cs | 120 | 0.00403 | 250 | 1.065 | 0.56 | 234.3
48-AL1/8-ST1A 0.4_air | 12.2 | 0.5939 | 0.3 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NAEKBA 3x120rm 12/20kV | 350 | 0.2534 | 0.10681 | 0.235 | cs | 120 | 0.00403 | 155 | 1.0136 | 0.42726 | 346.4
NA2YSY 1x150rm 12/20kV ir | 260 | 0.2092 | 0.11624 | 0.325 | cs | 150 | 0.00403 | 150 | 0.8367 | 0.46496 | 275.7
NKBA 4x70sm 0.6/1kV | 880 | 0.2707 | 0.069115 | 0.235 | cs | 70 | 0.00393 | 180 | 1.0827 | 0.27646 | 441.1
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
NKBA 4x120sm 0.6/1kV | 1140 | 0.1556 | 0.065973 | 0.32 | cs | 120 | 0.00393 | 180 | 0.6224 | 0.26389 | 606.5
NYY-J 4x35 | 0 | 0.52403 | 0.085137 | 0.156 | cs | 0 | 0.00393 | 160 | 2.0961 | 0.34055 | 0
NYM 4x50 | 0 | 0.38696 | 0.084823 | 0.185 | cs | 0 | 0.00393 | 160 | 1.5478 | 0.33929 | 0
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NYY-J 3x95SM 0.6/1kV | 1160 | 0.1941 | 0.07477 | 0.332 | cs | 95 | 0.00393 | 160 | 0.7766 | 0.29908 | 496.2
NYCY 4x16/16 | 800 | 1.15 | 0.089535 | 0.102 | cs | 0 | 0.00393 | 160 | 4.6 | 0.35814 | 480
NAYY-J 4x35 | 0 | 0.869 | 0.085137 | 0.123 | cs | 0 | 0 | 160 | 3.476 | 0.34055 | 0
NA2YSY 1x95rm 12/20kV ir | 230 | 0.3225 | 0.12566 | 0.265 | cs | 95 | 0.00403 | 150 | 1.29 | 0.50265 | 238.9
NYY-J 4x50 | 0 | 0.38696 | 0.084823 | 0.185 | cs | 0 | 0.00393 | 160 | 1.5478 | 0.33929 | 0
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
NAYBY 4x50sm 0.6/1kV | 710 | 0.6417 | 0.07854 | 0.14 | cs | 50 | 0.00403 | 160 | 2.5667 | 0.31416 | 312.4
NYY-O 3x240SM 0.6/1kV | 1390 | 0.0777 | 0.072571 | 0.458 | cs | 240 | 0.00393 | 160 | 0.3106 | 0.29028 | 643.2
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
NYY-O 3x150SM 0.6/1kV | 1320.0001 | 0.1255 | 0.073199 | 0.348 | cs | 150 | 0.00393 | 160 | 0.5021 | 0.2928 | 588.1
N2XS(F)2Y 1x400RM/35 12/20kV it | 368 | 0.0535 | 0.11153 | 0.671 | cs | 400 | 0.00393 | 250 | 0.214 | 0.44611 | 366.6
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
94-AL1/15-ST1A 0.4_air | 13.2 | 0.306 | 0.29 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NYY-J 3x150SM 0.6/1kV | 1320.0001 | 0.1255 | 0.073199 | 0.426 | cs | 150 | 0.00393 | 160 | 0.5021 | 0.2928 | 588.1
NAYCWY 3x120/120 | 1280 | 0.3221 | 0.073199 | 0.24 | cs | 0 | 0.00403 | 160 | 1.2884 | 0.2928 | 768
NYCWY 3x50/50 | 980 | 0.3878 | 0.077597 | 0.184 | cs | 0 | 0.00393 | 160 | 1.5512 | 0.31039 | 588
NAYY-J 3x35/35 | 0 | 0.869 | 0.085137 | 0.123 | cs | 0 | 0 | 160 | 3.476 | 0.34055 | 0
NYCWY 3x95/50 | 1160 | 0.19473 | 0.07477 | 0.272 | cs | 0 | 0.00393 | 160 | 0.77894 | 0.29908 | 696
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
24-AL1/4-ST1A 0.4_air | 11.25 | 1.2012 | 0.335 | 0.31 | ol | 150 | 0.00403 | 250 | 0 | 0 | 0
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
NAYY 4x150SE 0.6/1kV | 830 | 0.2067 | 0.080425 | 0.27 | cs | 150 | 0.00403 | 160 | 0.8267 | 0.3217 | 385.9
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NAYY 4x120SE 0.6/1kV | 840 | 0.2542 | 0.080425 | 0.24 | cs | 120 | 0.00403 | 160 | 1.0167 | 0.3217 | 385.9
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
NAEKBA 3x50rm 12/20kV | 240 | 0.6415 | 0.12252 | 0.14 | cs | 50 | 0.00403 | 155 | 2.5661 | 0.49009 | 248.1
NEKBA 3x50rm 12/20kV | 240 | 0.3913 | 0.12252 | 0.18 | cs | 50 | 0.00393 | 155 | 1.5653 | 0.49009 | 248.1
N2YSY 1x70rm 12/20kV ir | 200 | 0.2711 | 0.13195 | 0.285 | cs | 70 | 0.00393 | 150 | 1.0845 | 0.52779 | 211.3
MS-Leitungstyp_fiktiv | 0 | 0 | 0 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NAYY-J 4x50 | 0 | 0.641 | 0.084823 | 0.144 | cs | 0 | 0 | 160 | 2.564 | 0.33929 | 0
NA2YSY 1x240rm 12/20kV ir | 310 | 0.1292 | 0.10996 | 0.425 | cs | 240 | 0.00403 | 150 | 0.5167 | 0.43982 | 321.6
NAYY 4x240SE 0.6/1kV | 870 | 0.1267 | 0.079796 | 0.357 | cs | 240 | 0.00403 | 160 | 0.5067 | 0.31919 | 422.7
NYCWY 3x25/16 | 840 | 0.72796 | 0.080739 | 0.129 | cs | 0 | 0.00393 | 160 | 2.9118 | 0.32296 | 504
NEKBA 3x95rm 12/20kV | 310 | 0.1948 | 0.10996 | 0.27 | cs | 95 | 0.00393 | 155 | 0.7792 | 0.43982 | 314.3
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
NAEKBA 3x150rm 12/20kV | 370 | 0.2076 | 0.10367 | 0.265 | cs | 150 | 0.00403 | 155 | 0.8305 | 0.41469 | 374
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 1x240RM 0.6/1kV ir | 800 | 0.1258 | 0.17719 | 0.432 | cs | 240 | 0.00403 | 160 | 0.5033 | 0.70874 | 808.6
MS/FL-Al/St 95/15 (410107)_air | 10 | 0.304 | 0.373 | 1 | ol | 0 | 0.00403 | 80 | 0.452 | 1.464 | 4
NAYBY 4x95sm 0.6/1kV | 840 | 0.3208 | 0.075398 | 0.21 | cs | 95 | 0.00403 | 160 | 1.2833 | 0.30159 | 404.3
NKBA 0.6/1 kV 3x50/ 25sm | 680 | 0.387 | 0.087996 | 0.191 | cs | 50 | 0.00393 | 180 | 1.548 | 0.35198 | 408
NYY 4x6 | 0 | 3.084 | 0.10085 | 0.056 | cs | 0 | 0.00393 | 160 | 12.336 | 0.40338 | 0
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
NYY-J 4x120 | 0 | 0.15378 | 0.080425 | 0.313 | cs | 0 | 0.00393 | 160 | 0.61513 | 0.3217 | 0
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NKBA 0.6/1 kV 3x35/ 16sm | 590 | 0.524 | 0.090981 | 0.161 | cs | 35 | 0.00393 | 180 | 2.096 | 0.36392 | 354
NYY 4x1.5 | 0 | 12.1187 | 0.11498 | 0.026 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.45993 | 0
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
NKBA 4x50sm 0.6/1kV | 760 | 0.3914 | 0.069115 | 0.19 | cs | 50 | 0.00393 | 180 | 1.5656 | 0.27646 | 349.2
NS-Leitungstyp_fiktiv | 0 | 0 | 0 | 1 | cs | 0 | 0.00403 | 80 | 0 | 0 | 0
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
NYCWY 3x70/70 | 1120 | 0.26995 | 0.07477 | 0.227 | cs | 0 | 0.00393 | 160 | 1.0798 | 0.29908 | 672
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NYY-J 3x185SM 0.6/1kV | 1320.0001 | 0.1013 | 0.073199 | 0.483 | cs | 185 | 0.00393 | 160 | 0.405 | 0.2928 | 588.1
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
NAYCWY 3x35/35 | 960 | 0.86558 | 0.078854 | 0.123 | cs | 0 | 0.00403 | 160 | 3.4623 | 0.31542 | 576
NYY 4x2.5 | 0 | 7.4133 | 0.10681 | 0.034 | cs | 0 | 0.00393 | 160 | 29.6532 | 0.42726 | 0
NYCWY 4x35/16 | 960 | 0.52486 | 0.085137 | 0.157 | cs | 0 | 0.00393 | 160 | 2.0995 | 0.34055 | 576
NKBA 4x35sm 0.6/1kV | 590 | 0.524 | 0.091012 | 0.161 | cs | 35 | 0.00393 | 180 | 2.096 | 0.36405 | 590
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
NYY 4x4 | 0 | 4.6135 | 0.1065 | 0.044 | cs | 0 | 0.00393 | 160 | 18.4538 | 0.426 | 0
NA2XY 3x150sm 0.6/1kV | 610 | 0.207 | 0.069115 | 0.3 | cs | 150 | 0.00403 | 250 | 0.8281 | 0.27646 | 238.9
NYY 3x1.5 | 0 | 12.1187 | 0.10776 | 0.025 | cs | 0 | 0.00393 | 160 | 48.4747 | 0.43103 | 0

## trafo_std_types
| sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | vector_group | vk0_percent | vkr0_percent | mag0_percent | mag0_rx | si0_hv_partial | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
MSNS_0126 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0062 | 0.4 | 20 | 0.4 | 4.16 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0008 | 0.63 | 20 | 0.4 | 4.04 | 0.7627 | 0.556 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0138 | 0.63 | 20 | 0.4 | 4 | 0.83937 | 0.542 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0150 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0141 | 0.63 | 20 | 0.4 | 4.1 | 0.83063 | 0.819 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0089 | 0.4 | 20 | 0.4 | 3.74 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0060 | 0.4 | 20 | 0.4 | 3.825 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0091 | 0.4 | 20 | 0.4 | 3.87 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0087 | 0.4 | 20 | 0.4 | 3.98 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0163 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0059 | 0.8 | 20 | 0.4 | 4.2 | 0.875 | 0.8 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0080 | 0.63 | 20 | 0.4 | 4.1 | 0.85937 | 0.589 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0153 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0148 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0140 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0061 | 0.63 | 20 | 0.4 | 3.9 | 0.71 | 0.562 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0077 | 0.315 | 20 | 0.4 | 3.89 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0039 | 0.4 | 20 | 0.4 | 3.8 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0161 | 0.63 | 20 | 0.4 | 4.25 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0017 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0011 | 0.4 | 20 | 0.4 | 4.14 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0040 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0121 | 0.515 | 20 | 0.4 | 4.1 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0051 | 0.63 | 20 | 0.4 | 4.11 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
160 MVA 380/110 kV | 160 | 380 | 110 | 12.2 | 0.25 | 60 | 0.06 | 0 | Yy0 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0137 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0004 | 0.4 | 20 | 0.4 | 4.01 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0093 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0147 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0013 | 0.515 | 20 | 0.4 | 4 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0172 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0046 | 0.4 | 20 | 0.4 | 3.85 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0021 | 0.4 | 20 | 0.4 | 3.8 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0124 | 0.63 | 20 | 0.4 | 3.7 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0102 | 0.315 | 20 | 0.4 | 3.95 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0018 | 0.4 | 20 | 0.4 | 4.25 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0107 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0164 | 0.4 | 20 | 0.4 | 3.81 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0005 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0135 | 0.63 | 20 | 0.4 | 3.94 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0035 | 0.63 | 20 | 0.4 | 4 | 0.84317 | 0.566 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0181 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0073 | 0.4 | 20 | 0.4 | 3.9 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0123 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0067 | 0.4 | 20 | 0.4 | 4.13 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0167 | 0.63 | 20 | 0.4 | 4.04 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0081 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.25 MVA 10/0.4 kV | 0.25 | 10 | 0.4 | 4 | 1.2 | 0.6 | 0.24 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0086 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0195 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0149 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0128 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0146 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0047 | 0.63 | 20 | 0.4 | 4.3 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0106 | 0.63 | 20 | 0.4 | 3.95 | 0.78238 | 0.5945 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0015 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0198 | 0.515 | 20 | 0.4 | 3.9 | 1.0485 | 0.30191 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.25 MVA 20/0.4 kV | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | Yzn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0025 | 0.4 | 20 | 0.4 | 3.81 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0029 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0160 | 0.315 | 20 | 0.4 | 4 | 0.98413 | 0.35 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
40 MVA 110/10 kV | 40 | 110 | 10 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0054 | 0.2 | 20 | 0.4 | 4.22 | 1 | 0.2 | 0.3 | 150 | Yz5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0129 | 0.63 | 20 | 0.4 | 4.2 | 0.83238 | 0.581 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.63 MVA 20/0.4 kV | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0076 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0068 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.4 MVA 20/0.4 kV | 0.4 | 20 | 0.4 | 6 | 1.425 | 1.35 | 0.3375 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0194 | 0.63 | 20 | 0.4 | 4.2 | 0.81079 | 0.546 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0042 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0053 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0056 | 0.2 | 20 | 0.4 | 3.86 | 1 | 0.2 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0078 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0098 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0069 | 0.63 | 20 | 0.4 | 4.4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0101 | 0.63 | 20 | 0.4 | 4 | 0.71127 | 0.588 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0085 | 0.4 | 20 | 0.4 | 3.87 | 0.7625 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_1000 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0057 | 0.4 | 20 | 0.4 | 4.88 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.4 MVA 10/0.4 kV | 0.4 | 10 | 0.4 | 4 | 1.325 | 0.95 | 0.2375 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0063 | 0.4 | 20 | 0.4 | 3.81 | 0.9605 | 0.397 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
OR 40000/110 27332688 | 40 | 115.1 | 21 | 13.92 | 0.38255 | 19.613 | 0.05 | 150 | YNd5 | 0 | 0 | 100 | 0 | 0.9
63 MVA 110/20 kV | 63 | 110 | 20 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0156 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0009 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0142 | 0.2 | 20 | 0.4 | 4 | 1.15 | 0.22 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0044 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0028 | 0.63 | 20 | 0.4 | 4.01 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0131 | 0.63 | 20 | 0.4 | 3.9 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0012 | 0.63 | 20 | 0.4 | 6 | 0.0011111 | 0.00099 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0108 | 0.4 | 20 | 0.4 | 4.2 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0092 | 0.4 | 20 | 0.4 | 3.54 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0050 | 0.4 | 20 | 0.4 | 4.2 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0158 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
25 MVA 110/10 kV | 25 | 110 | 10 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0185 | 0.63 | 20 | 0.4 | 3.89 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0058 | 0.515 | 20 | 0.4 | 4.025 | 0.87039 | 0.475 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0041 | 0.4 | 20 | 0.4 | 4.5 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0003 | 0.715 | 20 | 0.4 | 4.1 | 0.86713 | 0.7 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0162 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0034 | 0.63 | 20 | 0.4 | 3.82 | 0.00063492 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0192 | 0.63 | 20 | 0.4 | 4.16 | 0.76651 | 0.552 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0043 | 0.4 | 20 | 0.4 | 4.27 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0191 | 0.63 | 20 | 0.4 | 3.98 | 0.45984 | 0.523 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
0.63 MVA 10/0.4 kV | 0.63 | 10 | 0.4 | 4 | 1.0794 | 1.18 | 0.1873 | 150 | Dyn5 | [5 empty] | hv | 0 | -2 | 2 | 0 | 2.5 | 0
MSNS_0113 | 0.4 | 20 | 0.4 | 4.1 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0133 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0196 | 0.4 | 20 | 0.4 | 3.79 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0109 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0097 | 0.63 | 20 | 0.4 | 4.15 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0104 | 0.4 | 20 | 0.4 | 4.05 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0014 | 0.4 | 20 | 0.4 | 3.9 | 0.6575 | 0.407 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0145 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0136 | 0.63 | 20 | 0.4 | 4.1 | 0.84317 | 0.844 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0175 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0036 | 0.4 | 20 | 0.4 | 3.75 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0001 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0020 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0052 | 0.63 | 20 | 0.4 | 4.05 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0019 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0079 | 0.4 | 20 | 0.4 | 3.8 | 0.75125 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0168 | 0.4 | 20 | 0.4 | 4 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0169 | 0.25 | 20 | 0.4 | 3.8 | 0.35 | 0.09 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
25 MVA 110/20 kV | 25 | 110 | 20 | 12 | 0.41 | 14 | 0.07 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0165 | 0.63 | 20 | 0.4 | 4.03 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0032 | 0.63 | 20 | 0.4 | 4.2 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0072 | 0.4 | 20 | 0.4 | 3.65 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0030 | 0.8 | 20 | 0.4 | 4.2 | 0.875 | 0.8 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0199 | 0.63 | 20 | 0.4 | 4.065 | 0.97048 | 0.784 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0177 | 0.63 | 20 | 0.4 | 3.77 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0120 | 0.4 | 20 | 0.4 | 4.45 | 1.2 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0016 | 0.4 | 20 | 0.4 | 3.48 | 1.05 | 0.43 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0088 | 0.515 | 20 | 0.4 | 4 | 0.93204 | 0.515 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0045 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0048 | 0.4 | 20 | 0.4 | 3.79 | 1.35 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0037 | 0.63 | 20 | 0.4 | 4.1 | 0.85714 | 0.6 | 0.3 | 150 | Dy5 | 3 | 0 | 100 | 0 | 0.9
40 MVA 110/20 kV | 40 | 110 | 20 | 16.2 | 0.34 | 18 | 0.05 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
63 MVA 110/10 kV | 63 | 110 | 10 | 18 | 0.32 | 22 | 0.04 | 150 | YNd5 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0
MSNS_0103 | 0.4 | 20 | 0.4 | 3.65 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0112 | 0.63 | 20 | 0.4 | 4 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0186 | 0.63 | 20 | 0.4 | 3.9 | 0.85714 | 0.6 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0074 | 0.4 | 20 | 0.4 | 4.1 | 1.05 | 0.43 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
MSNS_0170 | 0.63 | 20 | 0.4 | 4.12 | 0.77762 | 0.567 | 0.3 | 150 | Dyn5 | 3 | 0 | 100 | 0 | 0.9
100 MVA 220/110 kV | 100 | 220 | 110 | 12 | 0.26 | 55 | 0.06 | 0 | Yy0 | [5 empty] | hv | 0 | -9 | 9 | 0 | 1.5 | 0

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | bus | description | object
6 | bus | substat | object
7 | bus | folder_id | object
8 | bus | sernum | object
9 | bus | for_name | object
10 | bus | chr_name | object
11 | load | name | object
12 | load | bus | uint32
13 | load | p_mw | float64
14 | load | q_mvar | float64
15 | load | const_z_percent | float64
16 | load | const_i_percent | float64
17 | load | sn_mva | float64
18 | load | scaling | float64
19 | load | in_service | bool
20 | load | type | object
21 | load | description | object
22 | load | sernum | object
23 | load | for_name | object
24 | load | chr_name | object
25 | sgen | name | object
26 | sgen | bus | int64
27 | sgen | p_mw | float64
28 | sgen | q_mvar | float64
29 | sgen | sn_mva | float64
30 | sgen | scaling | float64
31 | sgen | in_service | bool
32 | sgen | type | object
33 | sgen | current_source | bool
34 | sgen | description | object
35 | sgen | sernum | object
36 | sgen | for_name | object
37 | sgen | chr_name | object
38 | switch | bus | int64
39 | switch | element | int64
40 | switch | et | object
41 | switch | type | object
42 | switch | closed | bool
43 | switch | name | object
44 | switch | z_ohm | float64
45 | switch | in_ka | float64
46 | ext_grid | name | object
47 | ext_grid | bus | uint32
48 | ext_grid | vm_pu | float64
49 | ext_grid | va_degree | float64
50 | ext_grid | slack_weight | float64
51 | ext_grid | in_service | bool
52 | ext_grid | s_sc_max_mva | float64
53 | ext_grid | s_sc_min_mva | float64
54 | ext_grid | rx_min | float64
55 | ext_grid | rx_max | float64
56 | ext_grid | r0x0_max | float64
57 | ext_grid | x0x_max | float64
58 | ext_grid | r0x0_min | float64
59 | ext_grid | x0x_min | float64
60 | ext_grid | description | object
61 | line | name | object
62 | line | std_type | object
63 | line | from_bus | uint32
64 | line | to_bus | uint32
65 | line | length_km | float64
66 | line | r_ohm_per_km | float64
67 | line | x_ohm_per_km | float64
68 | line | c_nf_per_km | float64
69 | line | g_us_per_km | float64
70 | line | max_i_ka | float64
71 | line | df | float64
72 | line | parallel | uint32
73 | line | type | object
74 | line | in_service | bool
75 | line | r0_ohm_per_km | float64
76 | line | x0_ohm_per_km | float64
77 | line | c0_nf_per_km | float64
78 | line | alpha | float64
79 | line | temperature_degree_celsius | float64
80 | line | description | object
81 | line | line_idx | float64
82 | line | folder_id | object
83 | line | section_idx | int64
84 | trafo | name | object
85 | trafo | std_type | object
86 | trafo | hv_bus | uint32
87 | trafo | lv_bus | uint32
88 | trafo | sn_mva | float64
89 | trafo | vn_hv_kv | float64
90 | trafo | vn_lv_kv | float64
91 | trafo | vk_percent | float64
92 | trafo | vkr_percent | float64
93 | trafo | pfe_kw | float64
94 | trafo | i0_percent | float64
95 | trafo | shift_degree | float64
96 | trafo | tap_side | object
97 | trafo | tap_neutral | float64
98 | trafo | tap_min | float64
99 | trafo | tap_max | float64
100 | trafo | tap_step_percent | float64
101 | trafo | tap_step_degree | float64
102 | trafo | tap_pos | int32
103 | trafo | tap_phase_shifter | bool
104 | trafo | parallel | uint32
105 | trafo | df | float64
106 | trafo | in_service | bool
107 | trafo | vk0_percent | float64
108 | trafo | vkr0_percent | float64
109 | trafo | mag0_percent | float64
110 | trafo | mag0_rx | float64
111 | trafo | si0_hv_partial | float64
112 | trafo | tap_set_vm_pu | float64
113 | trafo | description | object
114 | trafo | equipment | object
115 | line_geodata | coords | object
116 | bus_geodata | x | float64
117 | bus_geodata | y | float64
118 | bus_geodata | coords | object

## parameters
| version | format_version | OPF_converged | name
0 | 2.13.1 | 2.12.0 | FALSE | Gesamtnetz